## Room index
A. Regular room
Length of the room, L (m) = |  | 2.55
Width of the room, W (m) = |  | 5.75
Height of luminaire above working plane, Hm (m) = |  |  | 2.05
Therefore the room index Ri = | L x W
Hm (L + W)
= 13.55 x 5.8
2.05(13.55 + 5.8)
Ri = | 0.86174
B. Non- Regular room
Ri = L x W
Hm (L + W)
= Horizontal Area of the room
Hm (½ x Room Perimeter)
Area (m²)= | 9.38
Perimeter= | 13.849
Hm (m)= | 2.05
Therefore Room index = 143.377
2.05 x ½ x 57.29
Ri = | 0.66079

## Util. Factor
2x 36W 1200mm louvred- Louvrelux 2
C:W:F= 0.8:0.6:0.2
E.g R.I= 1.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.52 | 0.58 | 0.61 | 0.62 | 0.62
R.I= | 1.5
U.F | Uf = 0.52 + {(1.31 - 1.0) (0.58 - 0.52)}
(2.0 - 1.0)
Uf = | 0.55
E.g R.I= 2.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.52 | 0.58 | 0.61 | 0.62 | 0.62
R.I= | 2.31
U.F | Uf = 0.58 + {(2.31 - 2.0) (0.61 - 0.58)}
(3.0 - 2.0)
Uf = | 0.5893
2x 58W 1500mm Diffuser( Prismatic)-Diffusalux
C:W:F= 0.8:0.6:0.2
E.g R.I= 1.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.62 | 0.74 | 0.79 | 0.82 | 0.84
R.I= | 1.106
U.F | Uf = 0.62 + {(1.31 - 1.0) (0.74 - 0.62)}
(2.0 - 1.0)
Uf = | 0.63272
E.g R.I= 2.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.62 | 0.74 | 0.79 | 0.82 | 0.82
R.I= | 2.31
U.F | Uf = 0.74 + {(2.31 - 2.0) (0.79 - 0.74)}
(3.0 - 2.0)
Uf = | 0.7555
28W 2D Thorn Superclub
C:W:F= 0.8:0.6:0.2
E.g R.I= 1.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.3 | 0.38 | 0.41 | 0.43 | 0.44
R.I= | 1.31
U.F | Uf = 0.3 + {(1.31 - 1.0) (0.38 - 0.3)}
(2.0 - 1.0)
Uf = | 0.3248
E.g R.I= 2.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.3 | 0.38 | 0.41 | 0.43 | 0.44
E.g R.I= | 2.31
U.F | Uf = 0.38 + {(2.31 - 2.0) (0.41 - 0.38)}
(3.0 - 2.0)
Uf = | 0.3893
2x34W 300x1200mm Thorn Invincible
C:W:F= 0.8:0.6:0.2
E.g R.I= 1.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.33 | 0.41 | 0.45 | 0.47 | 0.48
R.I= | 1.31
U.F | Uf = 0.52 + {(1.31 - 1.0) (0.58 - 0.52)}
(2.0 - 1.0)
Uf = | 0.3548
E.g R.I= 2.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.33 | 0.41 | 0.45 | 0.47 | 0.48
R.I= | 2.31
U.F | Uf = 0.58 + {(2.31 - 2.0) (0.61 - 0.58)}
(3.0 - 2.0)
Uf = | 0.4224
1x 36W 1200mm Bare batten
C:W:F= 0.8:0.6:0.2
E.g R.I= 1.31
R.I | 1 | 2 | 3 | 4 | 5
U.F | 0.6 | 0.78 | 0.86 | 0.91 | 0.94
R.I= | 1.5
U.F | Uf = 0.52 + {(1.31 - 1.0) (0.58 - 0.52)}
(2.0 - 1.0)
Uf = | 0.69

## Luminaire Qty
Length (m)= | 2.575
Width (m)= | 5.8
Area (m²)= | 14.935
Uf = | 0.62
E (Lux)= | 300
Øn(lumens) = | 3450
Mf = | 0.85
N = | 1
n = A x E = |  | 21.60 x 500
Uf x Mf x Øn x N 0.6327 x 0.85 x 5400
n = | 2.4643 | ≈ | 2.4643
This gives | 2 | N No. single fluorescent fittings with an illuminance of
E = n x Uf x Mf x Øn / A = 2 x 0.6327 x 0.85 x 5400
21.605
E ( Lux) = | 243.4751

## Illuminance
Length (m)= | 3.725
Width (m)= | 5.8
Area (m²)= | 21.605
Uf = | 0.63272
E (Lux)= | 500
Øn(lumens) = | 5400
Mf = | 0.85
n = | 2
E = n x Uf x Mf x Øn / A = 2 x 0.6327 x 0.85 x 5400
21.605
E = | 268.8438