## Published Papers (2) (hidden)
The Use of Concrete Enclosed Reinforcing Rods as Grounding Electrodes
Step1. Select the type of concrete-encased grounding
Multiple concrete-encased rebar grounding electrodes in Hollow rectangular configuration
Step 2. Enter the values of the parameters below in the highlighted cells:
ρₒ the resistivity of surrounding medium (Ω-m) | 300
L the length of rod in (m) | 2
0.02
r1 the outer radius of rod (m) | 0.03
ρ1 the higher resistivity of (earth) in (Ω-m) | 200
r the radius of equivalent hemisphere | 2.5
d the spacing of electrodes | 4
N the total number of rods | 11
k given in graph | 6
M multiplier to obtain array resistance from single electrode reistance | 0.43182
Grounding resistance in ohms (Ω) | 77.1683
EQUIVALENT EQUATION OF EARTH RESISTANCE FOR RING ELECTRODE OF WIND TURBINE
Propose novel equivalent equation by author
p the soil resistivity in (Ω-m) | 300
a the radius of a cross-section of the ring in (mm²) | 0.4
d the burying depth of the ring in (m) | 4
re equivalent radius in (m) | 0.1
α improvement constant (fixed value) | 1.85
β improvement constant (fixed value) | 3.82
Earth Resistance (Ω) | 43.9951
Earthing System’s Design in Presence of Non-uniform Soil
proposed a practical method for earthing systems’ design in presence of two-layer soil
pk the uniform soil with resistivity (Ω-m) | 300
h the depth of the earth electrode (m) | 4
LT the total buried length of conductors (m) | 5
A the area occupied by the earth electrode (mm²) | 0.4
Earthig Resistance (Ω) | 476.3104
A SIMPLIFIED METHOD FOR CALCULATING THE IMPULSE RESISTANCE OF VERTICAL GROUNDING RODS
due to the low current resistance of the grounding rod
p the soil resistivity (Ω-m) | 42.3
re effective radius varying with the current crest value impulse current (m) | 0.025
l the length of rod (m) | 1
Impulse Resistance (Ω) | 25.0007
A Systematic Approach to Safe and Effective Earthing System Design
Resistance of a single vertical earth electrode to achieve R<=5 ohms
p the soil resistivity (Ω-m) | 200
a the nominal diameter of earthing electrode (m) | 0.02
N the number of joint electrodes (vertically installed) for individual point P | 6
Ln the nominal length of earthing electrode (m) | 2
Lr the total length of vertical earthing electrode (m) | 12
Earthing Resistance (Ω) | 8.9965
DESIGN AND CALCULATION OF AN EARTH ELECTRODE
Vertical rod
r resistivity (Ω-cm) | 2000
h depth of burial (cm) | 80
L total length (cm) | 60
d diameter of the rod (cm) | 0.5
Earthing Resistance (Ω) | 71.8105
Case where a vertical rod is driven through a high-resistivity superficial layer into a lower resistivity subsoil
r1 the resistivity of the upper layer (Ω-cm) | 3000
r2 the resistivity of the subsoil (Ω-cm) | 2000
h depth of burial (cm) | 80
L total length of the rod (cm) | 60
d diameter of the rod (cm) | 0.5
L' effective length of the ground rod (cm) | 33.3333
Earthing Resistance (Ω) | 174.5266

## Procedure FlowChart
Proposed Design Procedure of Earthing Systems for Low-voltage Installations
Yes
No
Start
Conduct Soil Resistivity Test on Accessible Field in Installation Site
Review Client Design Specification if available
Review National Requirements Documentation
End
Proceed for Final Detailed Design
Are the Values of Step & Touch Voltages & Resistance Acceptable?
Conduct Preliminary Layout Design of Earthing Electrode Configuration & Size & Earthing Conductor Size
Calculate Earthing Resistance using this Template
Determine Maximum Fault Current flowing through the Earthing System
Analyse Step & Touch Voltages
Modify Design

## BS-7430 Resistance
Earthing Resistance Calculations based on BS 7430
Step 1. Select the type of earthing from the drop-down list below:
Three strips set at 120° meeting at the star point all of equal length |  | Remarks
Step 2. Enter the values of the parameters below in the highlighted cells: | input values |  | Output Value: Resistance
ρ the soil resistivity, in ohm metres (Ωm) | 30 |  | 2.3841 | ohm (Ω)
L the total length of the strip, in metres (m) | 20 |  | Satisfactory for R<5 ohm, continue with initial design
h the depth of burial, in metres (m) | 1.5
d the diameter of round conductor or diameter of equivalent cross sectional area of the strip, in metres (m) | 0.016
2
1.8
3
Note on F7: Select the earthing type
Note on G11: Enter the value to each parameter in the cells below
Note on G18: Select number of rods

## BS-7430 Conductor Selection
Size of the Earthing Conductor
The average fault current in A (R.M.S) | 1000
Fault current duration in seconds | 1
Metal Material | Copper
Maximum Temperature (°C) | 350
R.M.S Current density for 1 second duration, k (A/mm²) with initial conductor temperature of 30°C | 201
initial conductor temperature conductor is 30°C | NO
T1 the initial temperature in °C | 38
T2 the final temperature in °C | 69
new k value in (A/mm²) | 71.7878
Type of joint suitable for use at the temperature selected | Welded or Brazed
Corresponding conductor cross-sectional area in (mm²) | 13.9299
The average value of fault current in (kA)
Material of the strip | Copper
Duration of fault current in (seconds) | 1
Maximum conductor Temperature | 200
Size of conductor | 38 x 6
36.3
The average value of fault current in (kA)
Current density at the surface of earth electrode
t the duration of earth fault in seconds | 10
p the resistivity of the soil in ohm metres (Ωm) | 50
The current density at the surface of earth electrode in (A/m²) | 339.7058
Selection of the material for an earthing conductor with respect to corrosion and mechanical strength
Material | Copper
Configuration | Solid round
minimum size of the earthing conductor | 50 mm², 8 mm diameter
Remarks
50 mm² (8 mm diameter) may be reduced to 28 mm² (6 mm diameter) in certain applications where mechanical strength is not an essential requirement. Consideration should in this case, be given to reducing the spacing of the fasteners.
Applicable for air termination rods only. For applications where mechanical stress such as wind loading is not critical, a 10 mm diameter, 1 m long maximum air termination rod may be used. Applicable for earth lead-in rods only.
Note on F7: Enter the value of average RMS value of fault current in (A)
Note on F8: (fixed value) This table is only applicable for the case of 1 second
Note on F9: Select the material of the conductor
Note on F10: Select the maximum Temperature value for the conductor It should be verified that the material is likely to be in the same location as the conductor will not be damaged or present a fire risk at the temperature selected.
Note on F11: This is a fixed value
Note on F12: Is the initial temperature of the conductor = 30°C ?
Note on F19: Ensure that you select the nearst standard value which is higher than this calculated value
Note on F26: Select the material type of the strip
Note on F27: Select the duration (in seconds) of the fault current
Note on F28: Select the maximum temperature (in °C) of the conductor
Note on F29: Select the conductor size
Note on F40: Enter the duration value of earth faults in s
Note on F41: Enter the value of the soil resistivity in ohm-m
Note on F49: Select the material of the earthing conductor
Note on F50: Select the configuration of the earthing conductor
Note on F52: Allowable tolerance: −3%

## IEEE Green Book
Earthing Resistance Calculations based on IEEE Green Book
| Step 1. Select the type of earthing from the drop-down list below: |  | Remarks
One ground rod
| Step 2. Enter the values of the parameters below in the highlighted cells: | input values |  | Output Value: Resistance
39.3999 | p the soil resistivity, in ohm metres (Ωm) | 20 |  | 11.9262 | ohm (Ω)
| a the radius of the rod, in metres (m) | 0.008 |  | Does not comply for 5 ohms. Review and modify design
| L the rod length, in metres (m) | 1.5
| d the depth of burial, in metres (m) | 1 | 2
0.0001
3
Case where a typical electrode of 3 m long is used
| Diameter in (mm) | 12.7
| Soil Resistivity in (ohm-cm) | 43000
| Number of rods | 3
| Resistance value in ohm (Ω) | 192.6042
Does not comply for 5 ohms. Review and modify design
Note on F7: Select the earthing type
Note on G11: Enter the values on the orange cells below
Note on F21: Commonly used rod with length of 3 metres
Note on G22: Select the diameter of the rod
Note on G23: Enter the resistivity value in (ohm-cm)
Note on G24: Select the number of rods used

## Substation Grounding (hidden)
Alternative earthing calculations for grids and rods
Grid
p the soil resistivity (Ω-m) | 200
r the radius of a thin circular plate (m) | 0.02
L combined length of conductor forming a grid (m) | 3
h the burial depth (m) | 4
A the grid or rod array area (m²) | 0.03
Grid Resistance "simplest formula for a grid" (Ω) | 2566.6667
Grid Resistance based on both IEEE80 and BS 7354 (Ω) | 1319.1617
Grid Resistance (given in another formula by IEEE-80) (Ω) | 327.3416
Single rod resistance
Cylinder
p the soil resistivity (Ω-m) | 200
d the diameter of the rod (m) | 0.03
L the length of the rod (m) | 2
r the radius of an equivalent hemisphere (m) | 0.023
Resistance of the rod (Ω) | 3385.7462
A Practical Approach for Determining the Ground Resistance of Grounding Grids
ground resistance of grounding grids with square meshes in uniform soils can be calculated
p the resistivity of the soil (Ω-m) | 24
A the area of one mesh of the grounding grid (m²) | 2.25
L the number of meshes in direction X | 4
W the number of meshes in direction Y | 2
Ground Resistance (Ω) | 2.3132
Substation grounding system resistance calculations using a FEM approach
Homogeneous earth structure
ρ the uniform resistivity of the soil (Ω·m) | 200
l the active length of the rod (m) | 3
d the diameter of the rod (m) | 0.023
Single Rod Resistance in uniform soil (Ω) | 66.3906
How to design an effective earthing system to ensure the safety of the people
Grid consisting of a vertical electrode in the ground
p the soil resistivity (Ω-m) | 300
L the buried length of the electrode (m) | 3
d the diameter of the driven electrode (m) | 0.03
Grid Resistance (Ω) | 90.4734
Resistance for the grid formed with few electrodes in parallel
p soil resistivity (Ω-m) | 300
L the buried length of the electrode (m) | 2
d the diameter of the electrode (m) | 0.024
h buried depth (m) | 4
h2 effictive burial depth (m) | 4.2
s distance between 2 parallel electrode (m) | 3
S distance from one electrode to the image of the other (m) | 5.0794
b equivalent radius off the electrode at the surface (m) | 1.0998
Grid Resistance (Ω) | 13.9036
Resistance of mesh grid consisting of multiple horizontal conductors buried
p soil resistivity (Ω-m) | 200
h buried depth (m) | 3
L the buried length of the electrode (m) | 2
d the diameter of the electrode (m) | 0.03
Grid Resistance (Ω) | 72.6833
Horizontal buried conductors resistance developed by Schwarz
ρ Resistivity of the soil layer in which the grid is buried (Ω-m) | 300
h the depth of burial (m) | 3
L Total length of grid conductor (m) | 2
A Grid area (m²) | 0.03
K1 Grid geometry related constant | 2
K2 Grid geometry related constant | 1.2
Resistance of the electrode system (Ω) | 1059.0978
Substation grounding system resistance calculations using a FEM approach
Single rod resistance in uniform soil in Homogeneous earth structure
p uniform resistivity of the soil (Ω-m) | 200
l the active length of the rod (m) | 2
d the diameter of the rod (m) | 0.02
Grounding Resistance (Ω) | 95.3571
Another expression proposed by Schwarz, Grounding Resistance (Ω) | 90.4734
Note on E23: Select the rod model

## IEC 60364
IEC 60364 Conductor Selection
Earthing Electrode
Material | Copper.
Surface | Tin.coated
Shape | Rope
Minimum Size | Cross- section al area = (25 mm²) ,,Diameter = (1.8 mm) for individual strands of wire ,,Thickness of coating/sheathing Individual value = (1 µm), Average value = (5 µm)
Remarks
Earthing Conductor (buried in the soil)
Corrosion Protection | Protected against corrosion
Material | Copper
Mechanical Protection | Mechanically protected
Minimum cross-sectional area: | 2.5 mm²
Supplementary Equipotential Bonding Conductor
Connection | Two (2) Exposed– conductive– parts
Protection Preference | Sheathed or Mechanically Protected
Minimum cross-sectional area | ≥ ½ of the smaller protective conductor connecting to the exposed–conductive–part
Protective conductors
A) Method 1
Cross-sectional area of line conductor (mm²) | 16
Is the protective conductor is of the same material as the line conductor? | YES
Material of Line Conductor | Copper
Factor "k" value of the line conductor | 226
Material of Protective Conductor | Copper
Protective Conductor Type | insulated protective conductors not incorporated in cables and not bunched with other cables
Conductor Insulation | 70 °C PVC
PVC insulated conductors of cross-sectional area > 300 mm² ? | YES
Polyethylene
Visible and in restricted area
90 °C PVC
Factor k value of the protective conductor | 133
103
128
Minimum cross-sectional area of the corresponding protective conductor (mm²) | 16
B) Method 2
Value of fault current (r.m.s) in A | 1000
Operating time of the protective device for automatic disconnection in s | 3
Conductor Material | Copper
Minimum cross-sectional area of the corresponding protective conductor (mm²) | 7.6639
Note on E5: Select the type of material of the electrode
Note on E6: Select the surface type
Note on E7: Select the shape of the electrode
Note on E16: Select the protection type against corrosion
Note on E17: Select the material of the conductor
Note on E18: Select the mechanical protection preference
Note on E24: Select the type of connection
Note on E25: Select the protection preference for the conductor
Note on E34: Enter the value of the cross-sectional area of the line conductor
Note on E35: Are the materials similar for both protective conductor and line conductor?
Note on E36: Select the line conductor material
Note on E37: Fixed value
Note on E38: Select the protective line material
Note on E40: Select the conductor insulation type
Note on E41: Is the cross sectional area > 300 mm² for the PVC insulated conductor ?
Note on E42: Select the type of Cable Covering
Note on E43: Select the condition
Note on E44: Select the type of Cable Insulation
Note on D53: applicable only for a disconnection time not exceeding 5 s
Note on E55: Enter the (r.m.s) value of the fault current
Note on E56: applicable only for disconnection times not exceeding 5 s
Note on E57: Select the material of the conductro

## Common Methods
Common Earthing Practices in Malaysia
Step 1. Select the type of earthing from the drop-down list below:
Single Rod Electrode
Step 2. Select the values of the parameters below in the highlighted cells:
R the target earthing resistance, in ohm (Ω) | 5
ρ the soil resistivity, in ohm metres (Ωm) | 30
d the diameter of each rod, (mm) | 25
Output Data:
Total length of rod required in metres (m)
Total length of rod required in metres (m) | 6.313
Total length of rod required in metres (m)
2m - 4m
1.5
Note on D7: Select the type of earthing
Note on E11: Select the earthing resistance
Note on E12: Select soil resistivity
Note on E13: Select rod diameter

## Other Methods
* | The Use of Concrete Enclosed Reinforcing Rods as Grounding Electrodes
Step1. Select the type of concrete-encased grounding
Multiple concrete-encased rebar grounding electrodes in Hollow rectangular configuration
Step 2. Enter the values of the parameters below in the highlighted cells:
| ρₒ the resistivity of surrounding medium (Ω-m) | 200
| L the length of rod in (m) | 1.5
| r the radius of the rod (m) | 0.016
| r1 the outer radius of rod (m) | 0.2
| ρ1 the higher resistivity of (earth) in (Ω-m) | 150
| r the radius of equivalent hemisphere | 2.5
| d the spacing of electrodes | 3
| N the total number of rods | 10
| k given in graph | 6
| M multiplier to obtain array resistance from single electrode reistance | 0.6
| Grounding resistance in ohms (Ω) | 70.3748
* | EQUIVALENT EQUATION OF EARTH RESISTANCE FOR RING ELECTRODE OF WIND TURBINE
Propose novel equivalent equation by author
| p the soil resistivity in (Ω-m) | 300
| a the radius of a cross-section of the ring in (mm²) | 0.4
| d the burying depth of the ring in (m) | 4
| re equivalent radius in (m) | 0.1
| α improvement constant (fixed value) | 1.85
| β improvement constant (fixed value) | 3.82
| Earth Resistance (Ω) | 43.9951
* | Earthing System’s Design in Presence of Non-uniform Soil
proposed a practical method for earthing systems’ design in presence of two-layer soil
| pk the uniform soil with resistivity (Ω-m) | 60
| h the depth of the earth electrode (m) | 5
| LT the total buried length of conductors (m) | 4.5
| A the area occupied by the earth electrode (mm²) | 0.5
| Earthig Resistance (Ω) | 94.1462
* | A SIMPLIFIED METHOD FOR CALCULATING THE IMPULSE RESISTANCE OF VERTICAL GROUNDING RODS
due to the low current resistance of the grounding rod
| p the soil resistivity (Ω-m) | 42.3
| re effective radius varying with the current crest value impulse current (m) | 0.025
| l the length of rod (m) | 1
| Impulse Resistance (Ω) | 25.0007
* | A Systematic Approach to Safe and Effective Earthing System Design
Resistance of a single vertical earth electrode to achieve R<=5 ohms
| p the soil resistivity (Ω-m) | 100
| a the nominal diameter of earthing electrode (m) | 0.016
| N the number of joint electrodes (vertically installed) for individual point P | 10
| Ln the nominal length of earthing electrode (m) | 1.5
| Lr the total length of vertical earthing electrode (m) | 15
| Earthing Resistance (Ω) | 3.8354
Satisfactory, continue with initial design
* | DESIGN AND CALCULATION OF AN EARTH ELECTRODE
Buried straight rod or wire
| r resistivity (Ω-cm) | 1000
| h depth of burial (cm) | 180
| L total length (cm) | 150
| d diameter of the rod (cm) | 0.016
| Earthing Resistance (Ω) | 19.3179
Case where a vertical rod is driven through a high-resistivity superficial layer into a lower resistivity subsoil
| r1 the resistivity of the upper layer (Ω-cm) | 3000
| r2 the resistivity of the subsoil (Ω-cm) | 2000
| h depth of burial (cm) | 80
| L total length of the rod (cm) | 60
| d diameter of the rod (cm) | 0.5
| L' effective length of the ground rod (cm) | 33.3333
| Earthing Resistance (Ω) | 174.5266

## illustrations
Copper Plate
Copper Strip
Three Parallel aligned rods |  | Two Parallel aligned rods
Reinforced Concrete Foundation

## Worksheeet (hidden)
Type | [9 empty] | n |  | E
Plate | [9 empty] | 2 |  | Vertical electrodes
Rod electrode | [9 empty] | 3 |  | Horizontal electrodes
Parallel connection of aligned rods | [9 empty] | 4
Strip straight run or round conductor electrodes | [9 empty] | 6
Mesh | [9 empty] | 8 (octagon form)
Electrode encased in low resistivity material (eg. conducting concrete) | [9 empty] | 8 (square form)
Three rods at the vertices of an equilateral triangle
Two strips set at right angles to each other meeting at one corner
Three strips set at 120° meeting at the star point all of equal length
Four strips set in a cruciform
Vertical electrodes arranged in a hollow square
Reinforced concrete foundation
Horizontal strip electrode
TypeIEEE |  |  | Material | Max T | Joint |  | yes |  |  | T | Copper | Aluminium
Hemisphere |  |  | Copper | 700 | Welded |  | YES | Copper | 1 | 150 | 20 x 3 | 20 x 3
One ground rod |  |  | Aluminium | 600 | Brazed |  | NO | Aluminium | 3 | 200 | 25 x 3 | 25 x 3
Two ground rods s > L |  |  | Steel | 500 | Bolted |  |  |  |  | 250 | 25 x 4 | 25 x 6
Two ground rods s < L |  |  |  | 450 | Soft soldered |  |  |  |  | 300 | 25 x 6 | 50 x 6
Buried horizontal wire |  |  |  | 400 | [5 empty] | 450 | 31 x 3 | 60 x 6
Right-angle turn of wire |  |  |  | 350 | [5 empty] | 500 | 31 x 6 | 80 x 6
Three-point star |  |  |  | 300 | [6 empty] | 38 x 3
Four-point star |  |  |  | 250 | [6 empty] | 38 x 5
Six-point star |  |  |  | 200 | [6 empty] | 38 x 6
Eight-point star |  |  |  | 150 | [6 empty] | 50 x 3
Ring of wire |  |  |  | 100 | [6 empty] | 50 x 4
Buried horizontal strip | [10 empty] | 50 x 6
Buried horizontal round plate
Buried vertical round plate
|  |  | Material |  | Configuration
|  |  | Copper |  | Solid tape
|  |  | Tin plated copper |  | Solid round
|  |  | Aluminium |  | Stranded
Aluminium alloy
Galvanized steel
Stainless steel
M
Steel
Copper.
| Surface |  |  |  | Hot.dip.galvanized.or.Stainless |  |  | Copper.Sheathed |  | With.electrodeposited.copper.coating
| Hot.dip.galvanized.or.Stainless |  |  |  | Strip (as rolled strip or slit strip with rounded edges) |  |  | Round rod for deep earth electrode |  | Round rod for deeep earth electrodes
| Copper.Sheathed |  |  |  | Sections
| With.electrodeposited.copper.coating |  |  |  | Round rod for deep earth electrodes
| Bare |  |  |  | Round wire for surface electrode, depth not exceeding 0.5m
| Tin.coated |  |  |  | Pipe.
Zinc.coated
[5 empty] | Bare |  | Tin.coated | Zinc.coated
| Ty |  |  |  | Strip with rounded edges |  | Rope | Strip
| Protected against corrosion |  |  |  | Round wire for surface electrode with depth not exceeding 0.5m
| Not protected against corrosion |  |  |  | Rope,
[5 empty] | Pipe | [5 empty] | Simialr
| Mate | Mech |  |  | Connection |  | Prot |  |  |  | YES
| Iron | Mechanically protected |  |  | Two (2) Exposed– conductive– parts |  | Sheathed or Mechanically Protected |  |  |  | NO
| Copper | Mechanically unprotected |  |  | Exposed–conductive–part to extraneous–conductive– part |  | Not Mechanically Protected
Two (2) extraneous–parts
Ma
| Copper |  | Dia | Num | Typ | Insulation |  | Covering | Cableinsul | Condition
| Aluminium |  | 12.7 | 1 | insulated protective conductors not incorporated in cables and not bunched with other cables | 70 °C PVC |  | PVC | 70 °C PVC | Visible and in restricted area
| Lead |  | 15.88 | 2 | bare protective conductors in contact with cable covering but not bunched with other cables | 90 °C PVC |  | Polyethylene | 90 °C PVC | Normal conditions
| Steel |  | 19.05 | 3 | protective conductors as a core incorporated in a cable or bunched with other cables or insulated conductors | 90 °C thermosetting |  | CSP | 90 °C thermosetting | Fire risk
|  |  |  | 4 | protective conductors as a metallic layer of a cable e.g. armour, metallic sheath, concentric conductor, etc. | 60 °C rubber |  |  | 60 °C rubber
|  |  |  | 8 | bare conductors where there is no risk of damage to any neighbouring material by the temperature indicated | 85 °C rubber |  |  | 85 °C rubber
|  |  |  | 12 |  | Silicone rubber |  |  | Mineral PVC covered
|  |  |  | 16 |  |  |  |  | Mineral bare sheath
20
24
| Concrete | [7 empty] | Turbine |  |  | rod | Gomez
| Basic formula for Concrete-encased Rod Electrode | [7 empty] | Sunde's equation for electrode |  |  | Ellipsoid | Buried straight rod or wire
| Case where the ground is a dual nature medium | [7 empty] | Propose novel equivalent equation by author |  |  | Uniform current | Buried circle of wire
| Multiple concrete-encased rebar grounding electrodes in Hollow rectangular configuration | [10 empty] | Cylinder | Vertical rod
| Case |  | re | resss | dia |  | l
| Single Rod Electrode |  | 10 | 1 | 10 |  | 1.5
| Parallel Aligned Rods |  | 20 | 5 | 16
|  |  | 30 | 10 | 25
40
50
60
70
80
90
100