## POWERLINE Volt Drop
POWERLINE Voltage Drop Calculation
Standard Arctic BS6500
|  |  | Cable Size mm² | Single Phase
|  |  |  | Volt Drop mV/M/A | Current Capacity
|  |  | 2.5 | 19 | 25
|  |  | 4 | 12 | 32
Above figures for Voltage Drop are taken from BS7671:2008 Table 4F3B (Appendix 4)
Above figures for current Capacity are taken from BS7671:2008 Table 4F3A (Appendix 4)
|  | Total Volt Drop = | Cable Length M x Current A x Volt Drop / Metre / Amp V/M/A
BS7671:2008, 525.1 'In the absence of any other consideration, under normal service conditions the
voltage at the terminals of any fixed current-using equipment shall be greater than the lower limit
corresponding to the product standard relevant to the equipment.'
BS7671:2008, 525.2 'Where fixed current-using equipment is not the subject of a product standard the
voltage at the terminals shall be such as not to impair the safe functioning of that equipment.'
BS7671:2008, 525.3 'The above requirements are deemed to be satisfied if the voltage drop between the
origin of the installation (usually the supply terminals) and a socket-outlet or the terminals of fixed
current-using equipment does not exceed that stated in Appendix 12.'
BS7671:2008, 525.4 'A greater voltage drop than stated in Table 12A (Appendix 12) may be accepted for
a motor during starting periods and for other equipment with high inrush currents, provided that it is verified
that the voltage variations are within the limits specified in the relevant product standard for the equipment
or, in the absence of a product standard in accordance with the manufactures recommendations.
BS7671:2008 Table 12A (Appendix 12) The voltage drop within each final circuit should not
exceed 3% for lighting and 5% for other uses.
Standard POWERLINE Strings
Strings are available in 25, 50 or 100M lengths of 2.5 or 4mm² 3 core Cable with T drops every 5 or 10M
Click to View Standard Product Data Sheet
WARNING!
Do Not Exceed a Total Load of 16Amps on any One POWERLINE String.
Click-On Cells with Blue Text to Modify Values, Results will be Displayed in Green
Any Warnings will be Displayed in Red and Full Results are Displayed in Below Table.
|  | Permitted Voltage Drop (%) | 5% | Other | Circuit Type
|  | Actual Voltage Drop (%) | 0% | 110 | Supply Voltage (V)
|  | Total Voltage Drop (V) | 0 | 10 | Number of Outlets
|  | Voltage at Last Outlet (V) | 110 | 10 | Distance Between Outlets (Metres)
|  | Min Continuous Trans (VA) | 0 | 2.5 | Conductor Size (mm²)
|  | Length of String (M) | 95 | 0 | Total Current (Amps)
16
POWERLINE Voltage Drop Result Table
|  | Socket | Cable length (Metres) | Current (Amps) | Voltage Drop at Socket | Voltage at Socket (V) | Current at Outlet (Amps)
|  | 1 | 5 | 0 | 0 | 110 | 0 | 0
|  | 2 | 15 | 0 | 0 | 110 | 0 | 0
|  | 3 | 25 | 0 | 0 | 110 | 0 | 0
|  | 4 | 35 | 0 | 0 | 110 | 0 | 0
|  | 5 | 45 | 0 | 0 | 110 | 0 | 0
|  | 6 | 55 | 0 | 0 | 110 | 0 | 0
|  | 7 | 65 | 0 | 0 | 110 | 0 | 0
|  | 8 | 75 | 0 | 0 | 110 | 0 | 0
|  | 9 | 85 | 0 | 0 | 110 | 0 | 0
|  | 10 | 95 | 0 | 0 | 110 | 0 | 0
|  | 11 | 0 | 0 | 0 | 0 | 0 | 0
|  | 12 | 0 | 0 | 0 | 0 | 0 | 0
|  | 13 | 0 | 0 | 0 | 0 | 0 | 0
|  | 14 | 0 | 0 | 0 | 0 | 0 | 0
|  | 15 | 0 | 0 | 0 | 0 | 0 | 0
|  | 16 | 0 | 0 | 0 | 0 | 0 | 0
|  | 17 | 0 | 0 | 0 | 0 | 0 | 0
|  | 18 | 0 | 0 | 0 | 0 | 0 | 0
|  | 19 | 0 | 0 | 0 | 0 | 0 | 0
|  | 20 | 0 | 0 | 0 | 0 | 0 | 0
|  | 21 | 0 | 0 | 0 | 0 | 0 | 0
|  | 22 | 0 | 0 | 0 | 0 | 0 | 0
|  | 23 | 0 | 0 | 0 | 0 | 0 | 0
|  | 24 | 0 | 0 | 0 | 0 | 0 | 0
|  | 25 | 0 | 0 | 0 | 0 | 0 | 0
|  | 26 | 0 | 0 | 0 | 0 | 0 | 0
|  | 27 | 0 | 0 | 0 | 0 | 0 | 0
|  | 28 | 0 | 0 | 0 | 0 | 0 | 0
|  | 29 | 0 | 0 | 0 | 0 | 0 | 0
|  | 30 | 0 | 0 | 0 | 0 | 0 | 0
|  | 31 | 0 | 0 | 0 | 0 | 0 | 0
|  | 32 | 0 | 0 | 0 | 0 | 0 | 0
|  | 33 | 0 | 0 | 0 | 0 | 0 | 0
|  | 34 | 0 | 0 | 0 | 0 | 0 | 0
|  | 35 | 0 | 0 | 0 | 0 | 0 | 0
|  | 36 | 0 | 0 | 0 | 0 | 0 | 0
|  | 37 | 0 | 0 | 0 | 0 | 0 | 0
|  | 38 | 0 | 0 | 0 | 0 | 0 | 0
|  | 39 | 0 | 0 | 0 | 0 | 0 | 0
|  | 40 | 0 | 0 | 0 | 0 | 0 | 0
|  | 41 | 0 | 0 | 0 | 0 | 0 | 0
|  | 42 | 0 | 0 | 0 | 0 | 0 | 0
|  | 43 | 0 | 0 | 0 | 0 | 0 | 0
|  | 44 | 0 | 0 | 0 | 0 | 0 | 0
|  | 45 | 0 | 0 | 0 | 0 | 0 | 0
|  | 46 | 0 | 0 | 0 | 0 | 0 | 0
|  | 47 | 0 | 0 | 0 | 0 | 0 | 0
|  | 48 | 0 | 0 | 0 | 0 | 0 | 0
|  | 49 | 0 | 0 | 0 | 0 | 0 | 0
|  | 50 | 0 | 0 | 0 | 0 | 0 | 0
Blakley calculator (version 2.0) Blakley Electrics Ltd.
Click to Zero Outlet Currents