## SAMPLE LOAD SCHEDULE
LOAD SCHEDULE
BASEMENT FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 117 | 0.07 | 1 | 8.19 | 10.2375
Sockets | 28 | 0.25 | 0.2 | 1.4 | 1.75
DP | 8 | 2.2 | 0.5 | 8.8 | 11
LAUNDRY | 1 | 30 | 0.5 | 15 | 18.75
PUMP ROOM | 1 | 30 | 0.5 | 15 | 18.75
SWIMMING POOL | 1 | 9 | 0.8 | 7.2 | 9
TOTAL |  |  |  | 55.59 | 69.4875
GROUND FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 275 | 0.07 | 1 | 19.25 | 24.0625
Sockets | 50 | 0.25 | 0.2 | 2.5 | 3.125
DP | 9 | 2.2 | 0.5 | 9.9 | 12.375
FB | 28 | 2.2 | 0.2 | 12.32 | 15.4
Kitchen | 1 | 40 | 0.6 | 24 | 30
BOILER ROOM | 1 | 7.5 | 0.5 | 3.75 | 4.6875
TOTAL |  |  |  | 71.72 | 89.65
FIRST FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 204 | 0.07 | 1 | 14.28 | 17.85
Sockets | 89 | 0.25 | 0.2 | 4.45 | 5.5625
DP | 20 | 2.2 | 0.5 | 22 | 27.5
3PH | 1 | 7.5 | 0.4 | 3 | 3.75
TOTAL |  |  |  | 43.73 | 54.6625
SECOND FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 207 | 0.07 | 1 | 14.49 | 18.1125
Sockets | 89 | 0.25 | 0.2 | 4.45 | 5.5625
DP | 22 | 2.2 | 0.5 | 24.2 | 30.25
3PH | 2 | 7.5 | 0.4 | 6 | 7.5
TOTAL |  |  |  | 49.14 | 61.425
TYPICAL 3RD & 4TH FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 214 | 0.07 | 1 | 14.98 | 18.725
Sockets | 70 | 0.25 | 0.2 | 3.5 | 4.375
DP | 22 | 2.2 | 0.5 | 24.2 | 30.25
3PH | 1 | 7.5 | 0.4 | 3 | 3.75
TOTAL |  |  |  | 45.68 | 57.1
TOTAL LOAD FOR 2 FLOOR |  |  |  | 91.36 | 114.2
ROOF TOP
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 93 | 0.07 | 1 | 6.51 | 8.1375
Sockets | 6 | 0.25 | 0.2 | 0.3 | 0.375
DP | 3 | 2.2 | 0.5 | 3.3 | 4.125
3PH | 1 | 7.5 | 0.4 | 3 | 3.75
TOTAL |  |  |  | 13.11 | 16.3875
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lifts | 2 | 7.5 | 0.6 | 9 | 11.25
ACs | 1 | 70 | 0.6 | 42 | 52.5
TOTAL |  |  |  | 51 | 63.75
TOTAL LOAD FOR PROJECT A |  |  |  | 375.65 | 469.5625
TOTAL LOAD |  |  |  | 375.65 | 469.5625
ALLOW FOR 20% EXPANSION FOR CABLE |  |  |  | 450.78 | 563.475
TOTAL LOAD ON GENERATOR |  |  |  | 333.65 | 417.0625
ALLOW FOR 20% EXPANSION |  |  |  | 400.38 | 500.475
RUNNING AT 85% LOAD |  |  |  | 471.0353 | 588.7941
SPECIFICATION OF GEN SET AND TRANSFORMER
RECOMMENDED TRANSFORMER TO KPLC APPROVAL |  |  |  |  | 630KVA
STANDBY GENERATOR RATING |  |  | 480 KW | @ | 0.8 PF
GEN SET MODEL: |  |  | CAT C18-550
DIESEL ENGINE |  |  | CATERPILLAR
DIMENSIONS: LxWxH (mm) |  |  | 5880X1900X2550
WEIGHT: |  |  | 5100kg
|  |  | GEN SET |  | MAINS
LOAD CURRENT(Amps) |  |  | 696.2646 | AMPs | 783.9107
GENSET CABLE |  |  | 2 X185mm2 PER PHASE
MAINS CABLE |  |  | 2x240mm2 PER PHASE