PART F:

GENERAL AND PARTICULAR SPECIFICATIONS FOR MASTER CLOCK SYSTEM INSTALLATION

- FUNCTIONAL SPECIFICATIONS

- PARTICULAR SPECIFICATIONS

- FUNCTIONAL SPECIFICATION FOR A GPS SYNCHRONIZED CLOCK SYSTEM     USING NETWORK TIME PROTOCOL AND POWER OVER ETHERNET

1.0 REQUIREMENTS

1.1 GENERAL SYSTEM REQUIRMENTS

The synchronized clock system shall meet or exceed the requirements of this specification in all aspects.

1.2 OPERATIONAL REQUIREMENTS AND ENVIRONMENTAL SPECIFICATIONS

Operational Requirements

The clock system shall be located and operated in an indoor environment, within the   parameters of a standard network configuration distribution methods, and utilizing

standard industry provided network equipment and a standard network configuration

including standardized POE distribution technology.

The clock system shall operate autonomously and provide software configuration options

for time zone offsets, automatic daylight saving time corrections without scheduled operator

Intervention or maintenance. The clock system shall be configured via software control

and shall allow for remote monitoring and configuration changes while providing password

protection.

Environmental specifications

The system shall operate under the following environmental conditions:

Operating Range: 32° F to 122° F (0° C to 50° C)

Storage Range: -40° F to 70° F (-40° C to 70° C)

Relative Humidity: 0-90%, non-condensing

Compliance specifications

All equipment shall be tested, labeled and certified by a nationally recognized and approved laboratory to meet the following low voltage safety and electromagnetic compliance

requirements testing.

- FCC, part15, Class B limits for radiated and line conducted emissions

- Electromagnetic Compatibility 89/336/EEC ; 92/31/EC ;93/68/EEC ; 2004/108/EC

- Low voltage directive 2006/95/EC

1.3 CLOCK ENGINEERING REQUIRMENTS AND PERFORMANCE

The network clocks shall meet the following engineering and performance requirements.

1.3.1 Network clock engineering general specification:

The network clocks shall be designed to provide years of reliable and maintenance free service and shall be constructed of all metal enclosures with high impact, UV stable lenses to  ensure structural integrity and maximum durability. A wall mounting bracket, or other means, shall be provided for mounting to the surface of a wall.

The finish of the network clocks shall be of a high quality, durable, painted textured powder

coated finish and available in a choice of colors.

The network clocks enclosure shall be available in optional unpainted stainless steel material

and finish for special applicatios.

The network clocks shall be available in double faced or dual mount options for applications in  hallways or corridors.

The network clocks shall be designed for easy, cost effective,and reliable installation and use  standard RJ45, 10MB Ethernet style connectors.

Accuracy:

The networks clock displays shall be accurate to within 50 milliseconds of the UTC time  reference provided by the NTP server(s), when synchronized.

Protocol:

The Ethernet wired clocks shall support the following protocols:

SNTP, Simple Network Time Protocol

The network clocks shall operate with an internal reference time that is set to UTC (Universal Coordinated Time) via a built in the SNTP client, from up to two NTP timeservers. Primary and secondary servers shall be automatic, but configurable by either static IP

address or  Selection of the DHCP provided IP address configuration methods.

The network clocks shall be configurable to operate as an SNTP client in the following

operational modes: unicast (or query), broadcast, or multicast.

DHCP, Dynamic Host Configuration Protocol

The network clocks shall utilize DHCP (Dynamic Host Configuration Protocol), by default, as ameans of automating the configuration of all required network settings utilizing the optional settings area of a DHCP serve. All DHCP network and optional NTP settings shall allow

for enabling or disabling at each clock, in order to use static IP address mode network and NTP

settings.

Power:

The network clocks shall utilize a standardized Power over Ethernet (POE) technology to

power the clock in compliance with the IEEE 802.3af Power over Ethernet specification. The

network clocks shall be considered to be and to operate as Powered Devices (PD); and shall

utilize a 48V DC nominal voltage supplied over the spare Ethernet network cable pairs,

and/or the shared data/pairs, from an IEEE 802.3af compliant Power Sourcing Equipment

(PSE) device, with a  10/100 MB rating, for a distance of up to 100m (328 ft).

Power consumption shall be less than 12.95 Watts maximum for all PD equipment.

Each network clock PD shall have a typical power rating of less than 7.5 W.

The network clocks shall be made available with an optional AC power.  The power input shall  be made as a universal type with an input power range of 90-264 VAC, 47- 63 Hz and utilizing

a standard IEC power jack.

Connectors:

Type Connector

Ethernet 10/100 Base-T: RJ45The network clock system shall utilize standard Cat 5 or Cat 6 cablingfor the distributionof either data, or data and power using the same standard cable, and eliminating the need for an AC power source at the clock location.

Configuration settings:

The time displayed on the face of the networkclocks may either be UTC time or local time and  shall be configurable via software.

Clock displays shall offer flexibility to allow for any international time zone offset and automatic Daylight Saving Time (DST) adjustment and shall provide maintenance free reliable operation.  Configuration changes shall be retained in non-volatile flash.

The network clocks shall utilize an internal maintenance free rechargeable battery backed real time clock (RTC) to retain the internal time in the event of a power outage or for conditions  when the NTP server(s) is not available.  The network clocks shall not display the time during a power outage, but shall recover from such power outage as a system without intervention.

During such “free wheeling” periods and while in operation, the network clocks shall

provide a visual indication that the device is relying on the internal oscillator and is not

currently synchronized to the network timeserver.

2.3.2 Analog clock engineering specification:

The shape of the analog clock shall be round 12.5” [30 cm] or 18.” [45 cm]. The face of the  clock shall be off-white, the time indication marks on face shall be black.

The hour markings shall be in a Numeric format and in an easily read font. Minute / second marking shall be provided. The analog clock shall have black hour and minute hands and a red secondhand indicator.

The analog clock shall contain a stepper motor drive and state of the art microprocessor and

electronics control to rapidly syncronize the hands on the face of the clock to an accurate NTP

(Network Time Protocol) reference.

The stepper motor drive and gear system shall be of all metal construction for long

Maintenance free life andhigh product reliaility. The gear and drive train system shall be  smooth and quiet in operation to minimize motor noise.

An LED status indicator on the face of the clock shall illuminate when the clock is not  synchronized. The analog clock shall be available with the following options: LED illumination,double face ceiling or wall mount, stainless steel enclosure.

2.3.3 Digital clock engineering specification:

The displays shall utilize LED’s (Light Emitting Diodes) such that they are easy to read in  various lighting conditions, allow for large viewing angles, maximum-viewing distances,

long life expectance, and do not require back lighting.  The LED’s shall be  available in

various colors including red, amber, green, and blue displays for various visibility requirements

and in various sizes including 2.3” [5.8cm], 4” [10cm], and 8” [20cm] character heights.  In

addition, the brightnessof the LED display shall be fully adjustable via software to allow for

the display to be dimmed orbrightened remtely, in order to accommodate various lighting conditions and requirements.

2.0 CONFIGURATION SOFTWARE

The network clock system shall be fully configurable and managed remotely through IP via  software to simplify the costs associaed with administration.

GUI Interface – Windows configuration

The network clock system shall include a GUI (Graphical User Interface) based network  software application, operating under the Windows OS, for configuration andmaintenance of

[the network time server and] all network clocks.

The GUI application shall include password protection of the clock configuration, encrypted communication, and the ability to enable or disable options that might reduce security. A status display to remotely monitor the time displayed on the clock, the internal UTC time,

Synchronization status and any error condition regarding the clocks network status shall

be provided.

An optional advanced Windows based GUI configurationsoftware package shall be available for separate purchase, for quickly configuring groups of clocks with the ability to save and load

configurations.

Console interface –

Unix/Linux, nonWindows platform configuration

A separate menu driven telnet console interface shall be provided for configuration, of the

network time server and network clocks on a non-Windows OS such as UNIX, Linux.

3.0 REPAIR AND MAINTENANCE

Designed as solid state devices, the clocks shall require no standard maintenance and shall

have no user serviceable or replaceable parts inside in order to reduce  the requirement

for on-site maintenance and repair personnel.

Any necessary firmware updates shall be made available and able to be applied on location.

Instructions and required update files shall be made available for download from the

manufacturer’s website.

A procedure for trouble- shooting typical installation, configuration, and operational issues

shall be supplied as part of the documentation, as part of the user manual.

The manufacturer shall make warranty repair and service,as well as non- warranty repair

service, available.

- PARTICULAR TECHNICAL SPECIFICATIONS

- NTP MASTER CLOCK SERVER SPECIFICATIONS

    - BASIC FEATURES

Reference Sources

NTP ‐ client via 10/100 Mb Ethernet

High stability TCXO oscillator ± 1 min/year

Manual time set

GPS Internal Module Installed

Outputs

PPS

Programmable relay closure

Setup & Configuration Software

WinDiscovery network

Telnet software for UNIX/LINUX

MCRSET Windows

Programmable Relay

Schedule 1 event per day relay closure with N/O relay contact, 24V ‐ AC/DC (250 ma max)

    - OPTIONAL FEATURES

Reference Sources

Ultra stable oscillator ± 250 ms (1/4 sec.) year

Time code basic – IRIG B and SMPTE / EBU

Time code advanced – IRIG A and E

Outputs

NTP – server via 10/100 MB Ethernet

Time code basic – IRIG B and SMPTE / EBU

Time code advanced – IRIG A and E

NMEA 0183 via RS232 & USB

PPS and PPO pulse output

10MHz high stability sine wave

DB9 – Breakout Adapter

2  or 1 each 6 Digit Red LED Display

Basic Relay Scheduler ‐ Multiple events/day software (up to 128/day)

- NETWORK SWITCHES

2.01 48  port  PoE  switch

Technical Requirements

- To have (48)  10/100   Ethernet  ports

- 2  shared  Gigabit  combo  ports  and  2   Gigabit  uplink  ports

- Standards‐based  IEEE  802.3af  Power  over  Ethernet  (PoE) compliant  ‐   Up  to  24  ports  at  15.4W  for  375W  of  total  PoE  power

- To have Secure  management  via  SSH/SSL  and  secure  user  access   via  802.1x  Port  Authentication  and  MAC  address  filtering.

2.0.2 24  port  PoE  switch

Technical Requirements

- To have (24)  10/100   Ethernet  ports

- Standards‐based  IEEE  802.3af  Power  over  Ethernet  (PoE) compliant ‐   Up  to  12  ports  at 15.4W  for 180W  of  total  PoE  power

- Capable of handling high  gigabit  speeds  in the  network,  addressing  the   needs  of  power  users  and  high  bandwidth  applications

- Capable of providing  network  security;  secure  user  control  via  802.1x   port  authentication  and  MAC  address  filtering

- Should Provide  intelligent  traffic  management  with  rate  limiting,   policing,  shaping,  and  multicast  support .

- DIGITAL CLOCKS

- The clocks should be a Red/Blue seven-segment LED display with 4-inch numerals that are visible at over 150 feet (more than 50m)

- They should be powered through PoE.

- Time shall be automatically set by through a Network Protocol Time Server (NTP) server.

- The clocks shall have in-built checking mechanisms which relate to the real time of the NTP Master Control.

FEATURES

- 2.3"  (5.8cm),   6  digit   or 4digit LED  –  display  colors   in  red,  green,  amber,  and  blue

- Syncs  to  external  or  internal  NTP  source  for  accurate  traceable  time

- Display  time  in  12  or  24  hr  format  –  hh:mm:ss

- Display  date  ‐ MM:dd:yy  or  dd:MM:yy  or  yy:MM:dd  –  configurable

- Adjustable  brightness  levels

- All  international  time  zones  and  automatic  daylight  saving  times

- Standard  chassis  colors  should be black  or  beige  (off‐white)  powder  coat

- Power‐over‐Ethernet  or  –  worldwide  AC  Power

SPECIFICATIONS

Setup  and  control  software

- Supports  DHCP/BOOTP  for  automatic  acquisition  of  network  address,  nameservers,  and  time  server  configuration

- NTP  synchronization  options  and  more

- Provides  dynamic  configuration  for  networking  parameters,  time  zone/daylight  saving  time

- Configure  clocks  through  provided  network  discovery  tool  or  TELNET

- Network  discovery  tool  provides  automatic  discovery  of  NTP  clocks  attached  to  network  without  changing  PC’s  network  configuration

- Configuration  is  saved  to  non‐volatile  memory  and  survives  power  losses

- Encrypted  network  messages  prevent  unauthorized  tampering  of  clock  configuration

Connectors

- Ethernet – RJ45

- USB connector for setup (option)

- 2.1mm locking DC input jack (DC option)

Power

- Power consumption < 13W

- PoE (to IEEE 802.3af standard) or

- AC option ‐ International 115/230, 50/60 Hz

- Supplied with  British  power cord.

- DC option

- Includes external AC to DC wall‐mount power supply with locking DC plug

- International AC – 115/230, 50/60 Hz

- Supplied as  British option

- ANALOG CLOCKS

FEATURES

- Standard 12.5” (30cm) or Large 18” (45 cm) clock for easy viewing

- Uses NTP source for accurate time traceable to NIST  All international time zones

- Daylight saving time – available and configurable for all countries

- Uses standard Ethernet wiring

- Utilizes microprocessor controlled stepper motor

- Sweep second hand

- Optional Universal AC input voltage & frequency

- PoE (Power over Ethernet)

- Optional faceplate illumination – white

- Internal crystal and clock chip

- LED Status Indicator

- Deluxe handmade stainless steel chassis

SPECIFICATIONS

Setup and control software

- Supports DHCP/BOOTP for automatic acquisition of  network address,  name servers,

and time server configuration

- NTP synchronization options and more

- Provides dynamic configuration for networking parameters, time zone/daylight saving time  Configure clocks through provided network discovery tool or TELNET

- Network discovery tool provides automatic discovery of NTP clocks attached to network

without changing PC’s network configuration

- Configuration is saved to non‐volatile memory and survives power losses

- Encrypted network messages prevent unauthorized tampering of clock configuration

Power

- 90‐265 VAC 50/60 Hz

- IEC AC power connector and  cord

- UK, EURO, plugs

- PoE (Power over Ethernet) option to be used

Compliance

- CE Marked

- FCC, Class B, Emissions