PART G – BILLS OF QUANTITIES

Supply / Installation of a New 1.0 MVA Sound – Proofed Prime Rated Generator

A.	PREAMBLE

1.	The Bills of Quantities shall be read in conjunction with the Notes to Tenderers, Preliminaries, General Conditions of Contract, Technical Specifications and Drawings.

2.	The rates and prices tendered in the priced Bills of Quantities shall, except in so far as it is otherwise provided under the Contract, include all Plant, equipment, labour, supervision, materials, erection, maintenance, insurance, profit together with all general risks, liabilities and obligations set out or implied in the Contract, including taxes and duties (including V.A.T)   The quantities given are provisional and are for guidance only.  The whole works shall be re-measured upon practical completion.

3.	A rate of price shall be entered against each item in the priced Bills of Quantities, whether quantities are stated or not.  The cost of items against which the Contractor has failed to enter a rate or  price shall be deemed to be covered by other rates and prices entered in the Bills of quantities.

4.	The whole cost complying with the provision of the contract shall be included in the Items provided in the Bills of Quantities, and where no items are provided the cost shall be deemed to be distributed among the rates and prices entered for the related Items of Work.

5.	General directions and descriptions of work and materials are into necessarily repeated nor summarized in the Bills of Quantities. Reference to the relevant sections of the Contract documentation shall be made before entering prices against each item in the priced Bills of Quantities.

6.	Provisional Sums and contingencies included and so designated in the Bills of quantities shall be expanded in whole or in part at the direction and discretion of the Engineer.

7.	Errors in pricing will be corrected by the Client for any arithmetic errors in computation or summation as follows:-

  - Where there is a discrepancy between amount in figures and in words, the amount in words will govern and

b)	Where there is a discrepancy, between the unit rate and the total amount derived from the multiplication of the unit price and the quantity, the unit rate as quoted will govern, unless in the opinion of the Client, there is obviously gross misplacement of the decimal point in the unit prices, in which event total amount as quoted will govern and the unit rate will be corrected.

8.	The under listed information should accompany the tenders returned:-

a)	Company profile and Brochure of GENERATOR model offered detailing all the featured of interest and reference sites of similar installation.

b)	Equipment guarantee (by Contractor) and Warranty period specified by the manufacturer.

c)	Valid Certificate of Registration by the Ministry of Energy and dealership Licence (or appointment letter) from the Parent/Brand Company.

- A copy of V.A.T registration certificate.

- A copy of P.I.N Registration certificate.

BILL No.1 - TOOLS

The following tools shall be handed over to the Client or Engineer before completion of the contract:-

| Item | Description | Price (Ksh.) |
| --- | --- | --- |
| 1. 2. 3. 4. 5. 6. 7. 8. | Metal tool box with locks Set of 8 No. Chrome vanadium ring spanners in sizes to suit the set Set of 8 No. Chrome vanadium open-ended spanners in sizes to suit the set Set of screwdrivers, 75mm, 200mm and 300mm plus one 200 mm Philips type One set of feeler gauges One grease gun to suit greasing points One oil can, trigger type One Hydrometer and plastic filler bottle with pouring spout |  |
|  | Total carried forward to Bills Collection Page: G - 7 |  |

The tenderer shall give below details of any special tools, which he recommends should be purchased as an optional extra.

| Item | Description | Quantity | Unit Rates (Ksh.) |
| --- | --- | --- | --- |

Signed : (as in Tender) ………………………………………………………………………………….……

Date: …………………………………………………………..………………………………………………..

BILL No.2

LIST OF SPARE PARTS AND LUBRICANTS TO BE SUPPLIED WITH EACH SET

The following items shall be handed over to the Client or Engineer before completion of the contract.

These items shall not be used by the Contractor to carry out his normal maintenance.

| Item | Description | Price (Ksh.) |
| --- | --- | --- |
| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11 | Oil Filters – 3 Nos. Air Filters – 3 Nos. One injector to suit the set One set of fan belts comprising …………………….…………. belts One set of indicator bulbs comprising ………………..……… bulbs One set of indicator lenses comprising ……..……………… lenses One overhaul kit One set of fuses comprising …………………………...………fuses One 200 litre drum of sump grade oil One 2 kilogram tin of grease of grade One 10 litre plastic container of distilled water |  |
|  | Total carried forward to Bills Collection Page: H - 7 |  |

The tenderer shall give below details of any other  spares, which he recommends should be purchased as optional extra

| Item | Description | Quantity | Unit Rates (Ksh.) |
| --- | --- | --- | --- |

Signed : (as in Tender) ……………………………………………………………………………………

Date: ……………………………………………………………………………………………………………

BILL No.3

EARTHING

| Item | Description | Price (Ksh.) |
| --- | --- | --- |
| 1 | Supply and install, for each set, 4No. steel cored copper earth rods, 1200mm x 12mm threaded for extension, connected by brass clamps to 30 metres of 25mm x 3mm copper earth tape laid in trenches of minimum depth 300mm and fixed to the wall of the generator room with brass spacer bar saddles at 1 metre of intervals, connected to the station earth bar via a brass test clamp |  |
|  | Total carried forward to Bills Collection Page: H- 7 |  |

NOTE:	THE EARTHING MUST BE CARRIED OUT STRICTLY AS ABOVE

Signed : (as in Tender) …………………………………………………………………………………

Date: ………………………………………………………………………………………………………..

BILL No.4

| Item | Description | Price (Ksh.) |
| --- | --- | --- |
| 1. 2. | EXTERNAL FUEL TANK Structural Drawings and Calculations 2No. copies of general arrangement and fabrication drawings properly dimensioned and detailed showing the whole tower and its accessories together with 2 No. copies of the structural calculations complying with all the relevant BS and CP are to be submitted for approval prior to the commencement of the work to allow the structural Engineer to design the foundations. Diesel Storage Tank 1000 litres (1m3) external diesel fuel tank. The tanks shall be pressed steel sectional tanks complying in all respect to BS 1564 Types 1 or 2. The jointing material shall be non-toxic and non insoluble to diesel and the tank cover shall be jointed throughout the tank top ensuring that the joint is both leak proof and dustproof. Cover framing and members shall be designed to withstand super imposed loadings complying with the requirements of CP3 chapter V part 1 and BS 449 part. All internal stays are to be provided as required by the tank manufacturer and the Contractor will be responsible for ensuring the stays are adequate in number and position and are properly tightened. The subcontract is to notify the Electrical Engineer of the type of panel he is proposing to use and the manufacturer for approval. Preferred Dimensions: 1.7metres length 1.7metres width 1.8metres depth The tank to be complete with the following: Manual hand-operated fuel transfer puma with hose connection -Connection for 40mm diameter class B Gms pipe with “CRANE” gate valve and union -4m long 15mm diameter class B Gms pipe -4 No. Galvanised malleable iron elbow -75mm diameter drain pipe with “CRANE” gate valve -Clear level indicating tubing connection of the outside -All other accessories -To be inaccordance with NEMA and Kenya Bureau of Standard including certification accordingly |  |
|  | TOTAL COST CARRIED FORWARD To Bill Collection Page G - 7 |  |

BILL No.5

| ITEM | DESCRIPTION | QTY | UNIT | RATE | ##### AMOUNT |
| --- | --- | --- | --- | --- | --- |
| No. |  |  |  |  | KSHS. |
| 1. 2. 3. 4. 5. 6. 7. 8. | SUPPLY, DELIVER, INSTALL, SET TO WORK AND COMMISSION THE FOLLOWING Two parallel running 4 core 50mm2 PVC/SWA/PVC copper cable running from the generator control panel to the AMF in ground floor 4 core 4mm2 PVC/SWA/PVC copper cable for control Allow for all the necessary cable glands and their accessories for termination of the cables in items 1 and 2 Allow for all the necessary copper tails linking the AMF panel to the main switch gear bus-bar 200A TP MCCB as Crabtree, or other equal and approved, to be installed inside the main switch gear Allow for extension of the generator exhaust system including all the necessary lagging and clanding Allow for termination of the generator supply to the main switch gear bus-bar, including all the necessary cable lugs, bolts, nuts and washers Allow for filling of the generator daily service tank with diesel during the testing/trial runs and commissioning of the generator set | 100 50 1 Item 1 30 Item 400 | LM LM Item Item No. LM Item LT. |  |  |
|  | # TOTAL COST CARRIED FORWARD Bills COLLECTION PAGE: G- 7 |  |  |  |  |

###### BILLS COLLECTION PAGE

##### Local Materials and Installation Bills

| ITEM No. | DESCRIPTION | KSHS. | CTS. |
| --- | --- | --- | --- |
| A. B. C. D. E. | SUPPLY OF TOOLS - BILL NO. 1 BROUGHT FORWARD………..…… SUPPLY OF SPARE PARTS AND LUBRICANTS - BILL NO. 2 BROUGHT FORWARD……………………………………………………… EARTHING - BILL NO. 3 BROUGHT FORWARD…………...…………… SUPPLY OF EXTERNAL FUEL TANK - BILL NO. 4 BROUGHT FORWARD ……………..………...……………………...…………………… SUPPLY OF LOCAL MATERIALS – BILL NO. 5 BROUGHT FORWARD…………………………………………………………………….. |  |  |
|  | ##### TOTAL COST FOR LOCAL COMPONENTS CARRIED FORWARD TO PRICE SUMMARY PAGE G - 9.…………………………………………………………………. |  |  |

BILL No.6

| ITEM | DESCRIPTION | QTY | UNIT | RATE |  | ##### AMOUNT |
| --- | --- | --- | --- | --- | --- | --- |
| No. |  |  |  |  |  | KSHS. |
| 1. 2. 3. | ###### IMPORTED COMPONENTS BILL SUPPLY, DELIVERY & INSTALLATION COMMISSION AND MAINTAIN OF 1 NO. 150 KVA 415V SOUND PROOFED STANDBY GENERATOR Price of materials C & F Mombasa, for 1 No. generator set, complete with complete with a daily service tank capable of running 12hrs continuous, all necessary components, accessories and as specified elsewhere in this and all other contract document. Automatic mains failure change-over panel, appropriately rated for the generator set, and to be complete with a manual by-pass switch Transportation of the equipments from the port to site Rate of Exchange ________________ Ksh. _________________ | Item Item Item | Item Item Item |  |  |  |
| # TOTAL COST FOR IMPORTED COMPONENTS CARRIED FORWARD To Price Summary Page G-9 |  |  |  |  |  |  |

PRICE SUMMARY

| ITEM No. | DESCRIPTION | KSHS. | CTS. |
| --- | --- | --- | --- |
| [1] A. B. C. D. E. [2] F. G. H. I. J. K. | IMPORTED COMPONENTS Total amount for the generator set brought forward from - Bill No. 6…… Marine Insurance ……………………………………………………………… Cost of clearing, forwarding, bank charges, agency fee and transport to site …………………………………..………………………………………….. Import Duty of imported materials ___________ % (state %)_________ Value Added Tax on imported materials ________% (state %)________ LOCAL MATERIALS AND ASSOCIATED WORKS Local materials and installation brought forward from Bills Collection Page 6…………………………………………………………………………. Testing and commissioning …………………………………………………. Allow for providing maintenance and instruction manuals, three sets…… Allow for the normal maintenance and periodical service during the 12 months warranty period, excluding the consumables…………………. Value Added Tax on Items, F G & H __________%(state %)_________ Contingency sum to be used for authorised variations only………………. | 500,000 | 00 |
| TOTAL FOR THE INSTALLATION OF 1 NO. 150 KVA, STANDBY GENERATOR CARRIED FORWARD TO FORM OF TENDER.............................. |  |  |  |
| Name of Tenderer ………………………………………………………………………………………………… Address: ……………………………………………….. Telephone: ……………………………………….. Signature: ……………………………………………….. Date: ……………………………………………… NOTE: Prices for the Items A to G by the Tenderer must be sufficient for the complete operation of 1 No. 150 KVA,standby Generator set. |  |  |  |