## GENERATOR
PROJECT A - ELECTRICAL SERVICES
GENERATOR INSTALLATION
Page 1
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
[5 empty] | KSHS | CTS
SUPPLY, DELIVER, INSTALL, TEST, & COMMISSION THE FOLLOWING.
1a | Sound attenuated 484KW (standby) at 0.8pf with consideration of derating factor as per the altitude indicated in the specifications, 75dbA diesel engine generator set, rated 3 phase, 415V 50Hz @ 1500 rpm suitable for AMF operation as CAT C18-605 | No. | 1
1b | Engine exhaust system ducting and piping including support structure including setting out layout to architects/Engineer's approval | No. | 1
1c | Radiator extract system to architects/Engineer's approved layout | No. | 1
1d | AMF panel IP31 complete with 800A TP Automatic Load Transfer switch, Emergency load manager Module, 800A load transfer contactors , KWH energy meter and all ancillary apparatus as per approved designed layout. | No. | 1
1e | Control panel to load transfer /AMF panel and in turn to the 2X185 mm2 per phase SWA PVC 4 core copper cable from generator to main LV switch board | No. | 1
1f | 2.5mm2 x 2 core PVC control cable between LV switch board, generator set and Load transfer / AMF panel | Lm | 120
1g | 2x185 mm square PVC SWA PVC 4C cable | Lm | 18
1h | Copper cable lugs and glands for 2x185mm 2 cable | Lot | 1
1i | Cable glands and lugs for control cable under Item 1f above | Lot | 1
1j | Supply and install daily service tank | No. | 1
1k | Supply and install control panel(s), (complete with ov/uv relays | No. | 1
| Total carried forward to next page ………. |  |  |  | 0
GENERATOR INSTALLATION
Page 2
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
[5 empty] | KSHS | CTS
B/F
2a | Supply and install both manual and automatic fuel transfer pump plus the necessary piping to interconnect the daily service tank and the fuel storage tank | No. | 1
2b | 5000 litres external fuel tank | No. | 1
2c | Introduce external anti vibration dumpers to supplement the factory made ones | Lot | 1
2d | Trenching, sifting and backfilling 750mm deep trench for laying of ducts including compaction from generator to Main LV | Lm | 20
2e | Testing and Commissioning and any items necessary to complete the installation | Item | 1
2f | Cost of tools | Item | 1
2g | Cost of spares | Item | 1
2h | Cost of earthing as per | Item | 1
2i | Cost of drawings and manuals | Item | 1
2j | Cost of annual maintenance | Item | 1
2k | 6 Kg automatic self breaking fire extinguisher | No. | 1
| Total carried forward to summary page ………. |  |  |  | 10800000
SUMMARY OF TENDER PAGE
PROPOSED DESIGN AND SUPERVISION OF PROJECT A
GENERATOR INSTALLATIONS
Total Brought Forward from :
| : Page 2.…..……………………….…..………………….…. |  | KShs…………….… | 10800000
| Sub TotaI exclusive of VAT……………………………………… |  | Kshs…………........ | 10800000
| 16% VAT………………………………….……………………… |  | Kshs……………..... | 1728000
| Sub TotaI Inclusive of VAT……………………………………… |  | Kshs.…………..….. | 12528000
Add 5 % of sub totals(VAT inclusive) for contingency
| to be used for authorised variations…………………………….. |  | Kshs.…………….... | 626400
| TOTAL CARRIED TO FORM OF TENDER………………….... |  | KShs……. | 13154400
NB: Drawings are part of tender documents.Rates to include VAT and other relevant taxes
Name of Tenderer:...........................................................................................
Address of Tenderer:........................................................................................
| Signature and Stamp of Tenderer:.......................................... | Date: | .....………............

## LOAD SCHEDULE
LOAD SCHEDULE
BASEMENT FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 117 | 0.07 | 1 | 8.19 | 10.2375
Sockets | 28 | 0.25 | 0.2 | 1.4 | 1.75
DP | 8 | 2.2 | 0.5 | 8.8 | 11
LAUNDRY | 1 | 30 | 0.5 | 15 | 18.75
PUMP ROOM | 1 | 30 | 0.5 | 15 | 18.75
SWIMMING POOL | 1 | 9 | 0.8 | 7.2 | 9
TOTAL |  |  |  | 55.59 | 69.4875
GROUND FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 275 | 0.07 | 1 | 19.25 | 24.0625
Sockets | 50 | 0.25 | 0.2 | 2.5 | 3.125
DP | 9 | 2.2 | 0.5 | 9.9 | 12.375
FB | 28 | 2.2 | 0.2 | 12.32 | 15.4
Kitchen | 1 | 40 | 0.6 | 24 | 30
BOILER ROOM | 1 | 7.5 | 0.5 | 3.75 | 4.6875
TOTAL |  |  |  | 71.72 | 89.65
FIRST FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 204 | 0.07 | 1 | 14.28 | 17.85
Sockets | 89 | 0.25 | 0.2 | 4.45 | 5.5625
DP | 20 | 2.2 | 0.5 | 22 | 27.5
3PH | 1 | 7.5 | 0.4 | 3 | 3.75
TOTAL |  |  |  | 43.73 | 54.6625
SECOND FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 207 | 0.07 | 1 | 14.49 | 18.1125
Sockets | 89 | 0.25 | 0.2 | 4.45 | 5.5625
DP | 22 | 2.2 | 0.5 | 24.2 | 30.25
3PH | 2 | 7.5 | 0.4 | 6 | 7.5
TOTAL |  |  |  | 49.14 | 61.425
TYPICAL 3RD & 4TH FLOOR
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 214 | 0.07 | 1 | 14.98 | 18.725
Sockets | 70 | 0.25 | 0.2 | 3.5 | 4.375
DP | 22 | 2.2 | 0.5 | 24.2 | 30.25
3PH | 1 | 7.5 | 0.4 | 3 | 3.75
TOTAL |  |  |  | 45.68 | 57.1
TOTAL LOAD FOR 2 FLOOR |  |  |  | 91.36 | 114.2
ROOF TOP
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lights | 93 | 0.07 | 1 | 6.51 | 8.1375
Sockets | 6 | 0.25 | 0.2 | 0.3 | 0.375
DP | 3 | 2.2 | 0.5 | 3.3 | 4.125
3PH | 1 | 7.5 | 0.4 | 3 | 3.75
TOTAL |  |  |  | 13.11 | 16.3875
ITEM | NO | RATING | DIVERSITY | KW | KVA
Lifts | 2 | 7.5 | 0.6 | 9 | 11.25
ACs | 1 | 70 | 0.6 | 42 | 52.5
TOTAL |  |  |  | 51 | 63.75
TOTAL LOAD FOR ALBA HOTEL |  |  |  | 375.65 | 469.5625
TOTAL LOAD |  |  |  | 375.65 | 469.5625
ALLOW FOR 20% EXPANSION FOR CABLE |  |  |  | 450.78 | 563.475
TOTAL LOAD ON GENERATOR |  |  |  | 333.65 | 417.0625
ALLOW FOR 20% EXPANSION |  |  |  | 400.38 | 500.475
RUNNING AT 85% LOAD |  |  |  | 471.0353 | 588.7941
SPECIFICATION OF GEN SET AND TRANSFORMER
RECOMMENDED TRANSFORMER TO KPLC APPROVAL |  |  |  |  | 630KVA
STANDBY GENERATOR RATING |  |  | 480 KW | @ | 0.8 PF
GEN SET MODEL: |  |  | CAT C18-550
DIESEL ENGINE |  |  | CATERPILLAR
DIMENSIONS: LxWxH (mm) |  |  | 5880X1900X2550
WEIGHT: |  |  | 5100kg
|  |  | GEN SET |  | MAINS
LOAD CURRENT(Amps) |  |  | 696.2646 | AMPs | 783.9107
GENSET CABLE |  |  | 2 X185mm2 PER PHASE
MAINS CABLE |  |  | 2x240mm2 PER PHASE