## ELECTRICAL SERVICES
KAREN SDA Church - ELECTRICAL SERVICES
ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ1
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
PRELIMINARIES/GENERAL ITEMS
a | Allow for the preparation of all Working Drawings | 1 | Sum | 50000 | 50000
0
b | Allow for the preparation of all "As Built" Drawings | 1 | Sum | 50000 | 50000
0
c | The Tenderer is to describe hereunder inserting any relevant clause number, any other works, obligations or items that may be referred to in the Conditions of Contract, Specifications or Drawings in respect of the works for which he desires to enter a separate charge ( this charge is to be entered in the Amount column). If no charge is entered hereunder, rates and amounts elsewhere in the schedule of prices shall be deemed to cover all expenses for such works, obligations or items | 1 | Sum | 20000 | 20000
0
d | Allow for liaison and attendance to KPLC Ltd. in power application, and meter separation and installation of new 3phase meter. | 1 | Sum | 50000 | 50000
0
e | Allow for attendace to KPLC for the termination and energizing of the main low voltage board. | 1 | Sum | 25000 | 25000
0
f | Allow for provision of manuals | 1 | Sum | 3000 | 3000
0
g | Trenching and backfilling 2 X 100mm and 2 x 50 mm H/G PVC ductin a 450 mm wide by 600 deep Trench. | 50 | Lm | 750 | 37500
0
h | Construction of 450 mm by 450 mm x 600 mm Power Manhole | 1 | Sum | 7500 | 7500
0
i | Construction of 450 mm by 450 mm x 600 mm Tlecommunications Manhole | 1 | Sum | 7500 | 7500
0
j | Construction of 600 mm by 450 mm x 450 mm Service Turret Manhole | 1 | Sum | 7500 | 7500
0
k | PC SUM FOR KENYA POWER TRANSFORMER | 1 | Sum | 2000000 | 2000000
0
l | Any other necessary item(s) not included under the prelininaries |  |  |  | 0
| (i)…………………………………………….. |  |  |  | 0
| (ii) ………………………………………….. |  |  |  | 0
| Total carried forward to price summary page ………. |  |  |  | 2258000
BASEMENT ONE ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ2
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
LIGHTING
Final sub-circuits from distribution board in a cable and conduit/channel installation comprising concealed heavy gauge 20mm2 PVC conduit, 1.5 mm2 PVC insulated copper cables, 1.5 mm2 copper earthing cable including all accessories and fittings.
Supply, install, test and commsission,
a | Lighting point 1 & 2 way | 89 | No. | 1200 | 106800
0
0
b | 10 Amp one gang one way switch as MK | 3 | No. | 300 | 900
0
c | 10 Amp one gang two way switch as MK | 3 | No. | 300 | 900
0
d | 10 Amp four gang two way switch as MK | 4 | No. | 300 | 1200
| LIGHTING FITTINGS |  |  |  | 0
e | Type '6' 600x600mm, super efficient recessed LED modular luminaire with curved diffuser as V3 luminaires catalogue's ''LYTEPANEL LED RECESSED 600 x 600mm 4K'' or an approved equivalent. | 47 | No. | 6000 | 282000
0
f | Type '2A' 1200x300mm, 12W, super efficient recessed LED modular luminaire as V3 luminaires catalogue's ''RANA LED Recessed 1200 x 300mm double LED (2*LH)'' or an approved equivalent. | 4 | No. | 5500 | 22000
g | Type 'D2' 24W super shallow LED downlighter in round die cast aluminium housing for circulation spaces as V3 luminaires catalogue's ''Ascent 50 12 LED STD HO'' or an approved equivalent | 13 | No. | 5000 | 65000
0
h | Type 'WB' Bulkhead wall mounted light for the lift sahft as V3 luminaires catalogue's ''Sterling Bulkhead - LED - 3 Bar Grill'' or an approved equivalent. | 1 | No. | 4000 | 4000
0
i | Type 'WBR'Fashion LED Wall lamp as "Fashion industrial vintage Wall lamp industry simple European style lights wall sconces" or an approved equivalent. | 11 | No. | 7000 | 77000
0
j | Surface mounted double sided exit sign with 1X5W led lamps for BF- 4F maintained for 3 hours as OMS Emergency 2811 or equal and approved equivalent | 3 | No. | 5200 | 15600
j | Type 'LS' A very low glare miniature recessed LED wall light, delivering 94 lumens as brilliant lighting's 'LD42 LED wall light' or an approved equivalent | 10 | No. | 4000 | 40000
| Total carried forward to price next page ………. |  |  |  | 615400
BASEMENT ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ3
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
|  |  |  | B/F | 615400
Supply, install, test and commsission,
POWER OUTLET POINTS
a | 13A twin socket outlet point wired in 3X2.5mm2 PVC Copper cable in ring main | 8 | No. | 2000 | 16000
0
b | 20 Amp double pole outlet point wired in 3x4.0mm2 PVC Copper | 4 | No. | 2500 | 10000
0
c | 40A three phase outlet point wired in 4x6.0 mm2 PVC copper cable | 1 | No. | 3000 | 3000
0
| POWER ACCESSORIES |  |  |  | 0
0
d | 13A twin switched socket outlets as MK or an approved equivalent | 8 | No. | 500 | 4000
0
e | 20A DP switch outlet with neon light as MK or an approved equivalent | 4 | No. | 900 | 3600
0
f | 40A three phase socket outlet as MK or approved equivalent | 1 | No. | 1500 | 1500
0
| FIRE ALARM |  |  |  | 0
0
g | Addressable smoke/heat detectors as Menvier code MAOH850 plus addressable base with code MAB800 or approved equivalent | 5 | No. | 7000 | 35000
0
h | Addressable break glass as Menvier code MBG817 or approved equivalent | 1 | No. | 6000 | 6000
0
i | Sounder and beacon as Menvier code MASB870 or approved equivalent | 1 | No. | 8000 | 8000
0
j | Fire alarm initiating points wired in 1.5mm2 fire resistant cable enclosed in 20mm diameter conduits | 5 | No. | 2000 | 10000
0
0
| OTHER POINTS |  |  |  | 0
0
0
k | CCTV, Telephone,data & TV points in 20mm diameter Conduits | 9 | No. | 1100 | 9900
| Total carried forward to price summary page ………. |  |  |  | 722400
LOWER GROUND FLOOR ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ4
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
LIGHTING
Final sub-circuits from distribution board in a cable and conduit/channel installation comprising concealed heavy gauge 20mm2 PVC conduit, 1.5 mm2 PVC insulated copper cables, 1.5 mm2 copper earthing cable including all accessories and fittings.
Supply, install, test and commsission,
a | Lighting point 1&2 way | 283 | No. | 1200 | 339600
0
0
b | 10 Amp one gang one way switch as MK | 14 | No. | 300 | 4200
0
c | 10 Amp one gang two way switch as MK | 3 | No. | 300 | 900
0
d | 10 Amp four gang two way switch as MK | 12 | No. | 300 | 3600
e | 10 Amp two gang two switch as MK | 1 | No. | 300 | 300
| LIGHTING FITTINGS |  |  |  | 0
f | Type '6' 600x600mm, super efficient recessed LED modular luminaire with curved diffuser as V3 luminaires catalogue's ''LYTEPANEL LED RECESSED 600 x 600mm 4K'' or an approved equivalent. | 22 | No. | 6000 | 132000
0
g | Type '2C' 1200x300mm, 24W, super efficient recessed LED modular luminaire as V3 luminaires catalogue's ''RANA LED Recessed 1200 x 300mm single LED (1*LH)'' or an approved equivalent. | 19 | No. | 3000 | 57000
g | Ditto as above but with emergency kit | 5 | No. | 4200 | 21000
0
h | Type 'D2' 24W super shallow LED downlighter in round die cast aluminium housing for circulation spaces as V3 luminaires catalogue's ''Ascent 50 12 LED STD HO'' or an approved equivalent | 28 | No. | 5000 | 140000
0
i | Type 'WB' Bulkhead wall mounted light for the lift sahft as V3 luminaires catalogue's ''Sterling Bulkhead - LED - 3 Bar Grill'' or an approved equivalent. | 1 | No. | 4000 | 4000
j | Type '2D' 8W LED white downlight, IP44 rating for installation in wet areas as V3 luminaires catalogue's ''Insaver 150 HE Topper LED'' or an approved equivalent. | 70 | No. | 4600 | 322000
j | Surface mounted double sided exit sign with 1X5W led lamps for BF- 4F maintained for 3 hours as OMS Emergency 2811 or equal and approved equivalent | 3 | No. | 5200 | 15600
a | Type '6A' 1200x300mm, super efficient recessed LED modular luminaire as V3 luminaires catalogue's ''LYTEPANEL LED RECESSED 1200 x 300mm 4K'' or an approved equivalent. | 9 | No. | 3500 | 31500
b | Type 'D' Super efficient recessed LED adjustible downlight as V3 luminaires catalogue's ''Beacon Recessed Adjustable 26W'' or an approved equivalent. | 22 | No. | 5000 | 110000
c | Type 'SL' 21W (high output) Surface mounted luminaire as V3 luminaires catalogue's ''InVerto Direct NW Eb Rust'' or an approved equivalent. | 34 | No. | 4500 | 153000
d | Type 'ML' 600mm strip light ideal for over mirror lighting as 'Astro 0661' or an approved equivalent | 5 | No. | 2000 | 10000
e | Type 'LS' A very low glare miniature recessed LED wall light, delivering 94 lumens as brilliant lighting's 'LD42 LED wall light' or an approved equivalent | 55 | No. | 4000 | 220000
f | Type 'N' 2D 10 watt LED downlighter as NVC "NPX1021/10" or an approved equivalent. | 10 | No. | 4000 | 40000
| Total carried forward to price summary page ………. |  |  |  | 1604700
LOWER GROUND FLOOR ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ5
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
|  |  |  | B/F | 1604700
Supply, install, test and commsission,
POWER OUTLET POINTS
a | 13A twin socket outlet point wired in 3X2.5mm2 PVC Copper cable in ring main | 23 | No. | 2000 | 46000
0
b | 20 Amp double pole outlet point wired in 3x4.0mm2 PVC Copper | 5 | No. | 2500 | 12500
0
c | 40A three phase outlet point wired in 4x6.0 mm2 PVC copper cable | 6 | No. | 3000 | 18000
0
| POWER ACCESSORIES |  |  |  | 0
0
d | 13A twin switched socket outlets as MK or an approved equivalent | 23 | No. | 500 | 11500
0
e | 20A DP switch outlet with neon light as MK or an approved equivalent | 5 | No. | 900 | 4500
0
f | 40A three phase socket outlet as MK or approved equivalent | 6 | No. | 1500 | 9000
0
Supply, install, test and commsission,
| FIRE ALARM |  |  |  | 0
0
g | Addressable smoke/heat detectors as Menvier code MAOH850 plus addressable base with code MAB800 or approved equivalent | 15 | No. | 7000 | 105000
0
h | Addressable break glass as Menvier code MBG817 or approved equivalent | 2 | No. | 6000 | 12000
0
i | Sounder and beacon as Menvier code MASB870 or approved equivalent | 2 | No. | 8000 | 16000
0
j | Fire alarm initiating points wired in 1.5mm2 fire resistant cable enclosed in 20mm diameter conduits | 15 | No. | 2000 | 30000
0
0
| OTHER POINTS |  |  |  | 0
0
k | CCTV, Telephone,data & TV points in 20mm diameter Conduits | 42 | No. | 1100 | 46200
| Total carried forward to price next page ………. |  |  |  | 1915400
GROUND FLOOR ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ6
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
LIGHTING
Final sub-circuits from distribution board in a cable and conduit/channel installation comprising concealed heavy gauge 20mm2 PVC conduit, 1.5 mm2 PVC insulated copper cables, 1.5 mm2 copper earthing cable including all accessories and fittings.
Supply, install, test and commsission,
a | Lighting point 1 &2 way | 218 | No. | 1200 | 261600
0
b | 10 Amp one gang one way switch as MK | 20 | No. | 300 | 6000
0
c | 10 Amp one gang two way switch as MK | 2 | No. | 300 | 600
0
d | 10 Amp four gang two way switch as MK | 8 | No. | 300 | 2400
e | 10 Amp two gang two way switch as MK | 2 | No. | 300 | 600
| LIGHTING FITTINGS |  |  |  | 0
f | Type '6' 600x600mm, super efficient recessed LED modular luminaire with curved diffuser as V3 luminaires catalogue's ''LYTEPANEL LED RECESSED 600 x 600mm 4K'' or an approved equivalent. | 21 | No. | 6000 | 126000
0
g | Type '2C' 1200x300mm, 24W, super efficient recessed LED modular luminaire as V3 luminaires catalogue's ''RANA LED Recessed 1200 x 300mm single LED (1*LH)'' or an approved equivalent. | 30 | No. | 3000 | 90000
h | Ditto as above but with emergency kit | 4 | No. | 4200 | 16800
i | Type 'D2' 24W super shallow LED downlighter in round die cast aluminium housing for circulation spaces as V3 luminaires catalogue's ''Ascent 50 12 LED STD HO'' or an approved equivalent | 4 | No. | 5000 | 20000
0
j | Type 'WB' Bulkhead wall mounted light for the lift sahft as V3 luminaires catalogue's ''Sterling Bulkhead - LED - 3 Bar Grill'' or an approved equivalent. | 1 | No. | 4000 | 4000
0
k | Surface mounted double sided exit sign with 1X5W led lamps for BF- 4F maintained for 3 hours as OMS Emergency 2811 or equal and approved equivalent | 4 | No. | 5200 | 20800
j | Type 'LS' A very low glare miniature recessed LED wall light, delivering 94 lumens as brilliant lighting's 'LD42 LED wall light' or an approved equivalent | 68 | No. | 4000 | 272000
m | Type 'SL' 21W (high output) Surface mounted luminaire as V3 luminaires catalogue's ''InVerto Direct NW Eb Rust'' or an approved equivalent. | 6 | No. | 4500 | 27000
n | Type '2A' 1200x300mm, 12W, super efficient recessed LED modular luminaire as V3 luminaires catalogue's ''RANA LED Recessed 1200 x 300mm double LED (2*LH)'' or an approved equivalent. | 16 | No. | 5500 | 88000
o | Type 'FF' surface mounted linear luminaires in twin 2 x 24W T5 LED lamps complete with louvres for mounting. | 8 | No. | 2500 | 20000
p | Type 'N' 2D 10 watt LED downlighter as NVC "NPX1021/10" or an approved equivalent. | 50 | No. | 4000 | 200000
q | Type 'BL' Bulkhead IP65 surface ceiling downlight as NVC "MAXRD28/38-HF" or an approved equivalent. | 6 | No. | 3000 | 18000
| Total carried forward to price next page ………. |  |  |  | 1173800
GROUND FLOOR ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ7
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
|  |  |  | B/F | 1173800
Supply, install, test and commsission,
POWER OUTLET POINTS
a | 13A twin socket outlet point wired in 3X2.5mm2 PVC Copper cable in ring main | 21 | No. | 2000 | 42000
0
b | 20 Amp double pole outlet point wired in 3x4.0mm2 PVC Copper | 9 | No. | 2500 | 22500
0
c | 40A three phase outlet point wired in 4x6.0 mm2 PVC copper cable | 1 | No. | 3000 | 3000
0
| POWER ACCESSORIES |  |  |  | 0
0
d | 13A twin switched socket outlets as MK or an approved equivalent | 21 | No. | 500 | 10500
0
e | 20A DP switch outlet with neon light as MK or an approved equivalent | 9 | No. | 900 | 8100
0
f | 40A three phase socket outlet as MK or approved equivalent | 1 | No. | 1500 | 1500
Supply, install, test and commsission,
| FIRE ALARM |  |  |  | 0
0
g | Addressable smoke/heat detectors as Menvier code MAOH850 plus addressable base with code MAB800 or approved equivalent | 19 | No. | 7000 | 133000
0
h | Addressable break glass as Menvier code MBG817 or approved equivalent | 2 | No. | 6000 | 12000
0
i | Sounder and beacon as Menvier code MASB870 or approved equivalent | 2 | No. | 8000 | 16000
0
j | Fire alarm initiating points wired in 1.5mm2 fire resistant cable enclosed in 20mm diameter conduits | 19 | No. | 2000 | 38000
k | Intelligent Addressable 2-loop fire alarm panel complete with 72hrs standby batteries as Menvier DF60002 | 1 | No. | 150000 | 150000
0
| OTHER POINTS |  |  |  | 0
0
0
l | CCTV, Telephone,data & TV points in 20mm diameter Conduits | 44 | No. | 1100 | 48400
| Total carried forward to price summary page ………. |  |  |  | 1658800
FIRST FLOOR ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ8
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
LIGHTING
Final sub-circuits from distribution board in a cable and conduit/channel installation comprising concealed heavy gauge 20mm2 PVC conduit, 1.5 mm2 PVC insulated copper cables, 1.5 mm2 copper earthing cable including all accessories and fittings.
Supply, install, test and commsission,
a | Lighting point 1 & 2 way | 200 | No. | 1200 | 240000
0
0
b | 10 Amp one gang one way switch as MK | 15 | No. | 300 | 4500
0
c | 10 Amp one gang two way switch as MK | 1 | No. | 300 | 300
0
d | 10 Amp four gang two way switch as MK | 19 | No. | 300 | 5700
e | 10 Amp two gang one way switch as MK | 1 | No. | 300 | 300
0
| LIGHTING FITTINGS |  |  |  | 0
f | Type 'D2' 24W super shallow LED downlighter in round die cast aluminium housing for circulation spaces as V3 luminaires catalogue's ''Ascent 50 12 LED STD HO'' or an approved equivalent | 37 | No. | 5000 | 185000
0
g | Type 'WB' Bulkhead wall mounted light for the lift sahft as V3 luminaires catalogue's ''Sterling Bulkhead - LED - 3 Bar Grill'' or an approved equivalent. | 1 | No. | 4000 | 4000
h | Type 'LS' A very low glare miniature recessed LED wall light, delivering 94 lumens as brilliant lighting's 'LD42 LED wall light' or an approved equivalent | 43 | No. | 4000 | 172000
i | Type '2D' 8W LED white downlight, IP44 rating for installation in wet areas as V3 luminaires catalogue's ''Insaver 150 HE Topper LED'' or an approved equivalent. | 7 | No. | 4600 | 32200
j | Type 'N' 2D 10 watt LED downlighter as NVC "NPX1021/10" or an approved equivalent. | 16 | No. | 4000 | 64000
k | Type 'SL' 21W (high output) Surface mounted luminaire as V3 luminaires catalogue's ''InVerto Direct NW Eb Rust'' or an approved equivalent. | 6 | No. | 4500 | 27000
l | Type 'BL' Bulkhead IP65 surface ceiling downlight as NVC "MAXRD28/38-HF" or an approved equivalent. | 10 | No. | 3000 | 30000
m | Type 'D5' 2D 10 watt LED downlighter as NVC "NPX1021/10" or an approved equivalent. | 35 | No. | 4000 | 140000
n | Type 'WB1' Bedroom wall light with a separate LED reading light. The standard wall light should accommodate a low energy bulb and is supplied complete with the circular white fabric shade. As 'Peace chrome bedroom wall light SL-3550CC' or an approved equivalent | 14 | No. | 6000 | 84000
o | Type 'HB' LED Highbay luminaire as philips "BY688P LED 140/CW PSR S-WB" or an approved equivalent | 28 | No. | 5500 | 154000
p | Surface mounted double sided exit sign with 1X5W led lamps for BF- 4F maintained for 3 hours as OMS Emergency 2811 or equal and approved equivalent | 3 | No. | 5200 | 15600
| Total carried forward to price next page ………. |  |  |  | 918600
FIRST FLOOR ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ9
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
| B/F |  |  |  | 918600
Supply, install, test and commsission,
POWER OUTLET POINTS
a | 13A twin socket outlet point wired in 3X2.5mm2 PVC Copper cable in ring main | 23 | No. | 2000 | 46000
0
b | 20 Amp double pole outlet point wired in 3x4.0mm2 PVC Copper | 9 | No. | 2500 | 22500
0
c | 40A three phase outlet point wired in 4x6.0 mm2 PVC copper cable | 1 | No. | 3000 | 3000
0
| POWER ACCESSORIES |  |  |  | 0
0
d | 13A twin switched socket outlets as MK or an approved equivalent | 23 | No. | 500 | 11500
0
e | 20A DP switch outlet with neon light as MK or an approved equivalent | 9 | No. | 900 | 8100
0
f | 40A three phase socket outlet as MK or approved equivalent | 1 | No. | 1500 | 1500
0
Supply, install, test and commsission,
| FIRE ALARM |  |  |  | 0
0
g | Addressable smoke/heat detectors as Menvier code MAOH850 plus addressable base with code MAB800 or approved equivalent | 24 | No. | 7000 | 168000
0
h | Addressable break glass as Menvier code MBG817 or approved equivalent | 5 | No. | 6000 | 30000
0
i | Sounder and beacon as Menvier code MASB870 or approved equivalent | 5 | No. | 8000 | 40000
0
j | Fire alarm initiating points wired in 1.5mm2 fire resistant cable enclosed in 20mm diameter conduits | 24 | No. | 2000 | 48000
| OTHER POINTS |  |  |  | 0
0
0
k | CCTV, Telephone,data & TV points in 20mm diameter Conduits | 18 | No. | 1100 | 19800
| Total carried forward to Summary page ………. |  |  |  | 1317000
ROOF PLAN ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ10
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
LIGHTING
Final sub-circuits from distribution board in a cable and conduit/channel installation comprising concealed heavy gauge 20mm2 PVC conduit, 1.5 mm2 PVC insulated copper cables, 1.5 mm2 copper earthing cable including all accessories and fittings.
Supply, install, test and commsission,
a | Lighting point 1 & 2 way | 109 | No. | 1200 | 130800
0
0
b | 10 Amp three gang one way switch as MK | 2 | No. | 300 | 600
0
c | 10 Amp four gang one way switch as MK | 2 | No. | 300 | 600
0
0
| LIGHTING FITTINGS |  |  |  | 0
d | Type 'D2' 24W super shallow LED downlighter in round die cast aluminium housing for circulation spaces as V3 luminaires catalogue's ''Ascent 50 12 LED STD HO'' or an approved equivalent | 9 | No. | 5000 | 45000
0
e | Type 'WB' Bulkhead wall mounted light for the lift sahft as V3 luminaires catalogue's ''Sterling Bulkhead - LED - 3 Bar Grill'' or an approved equivalent. | 1 | No. | 4000 | 4000
f | Type 'LS' A very low glare miniature recessed LED wall light, delivering 94 lumens as brilliant lighting's 'LD42 LED wall light' or an approved equivalent | 6 | No. | 4000 | 24000
g | Type 'HB' LED Highbay luminaire as philips "BY688P LED 140/CW PSR S-WB" or an approved equivalent | 90 | No. | 5500 | 495000
m | Surface mounted double sided exit sign with 1X5W led lamps for BF- 4F maintained for 3 hours as OMS Emergency 2811 or equal and approved equivalent | 3 | No. | 5200 | 15600
| Total carried forward to price next page ………. |  |  |  | 584800
ROOF PLAN ELECTRICAL INSTALLATION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ11
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
|  |  |  | B/F | 584800
Supply, install, test and commsission,
POWER OUTLET POINTS
a | 13A twin socket outlet point wired in 3X2.5mm2 PVC Copper cable in ring main | 1 | No. | 2000 | 2000
0
b | 20 Amp double pole outlet point wired in 3x4.0mm2 PVC Copper | 1 | No. | 2500 | 2500
0
c | 40A three phase outlet point wired in 4x6.0 mm2 PVC copper cable | 1 | No. | 3000 | 3000
0
| POWER ACCESSORIES |  |  |  | 0
0
d | 13A twin switched socket outlets as MK or an approved equivalent | 1 | No. | 500 | 500
0
e | 20A DP switch outlet with neon light as MK or an approved equivalent | 1 | No. | 900 | 900
0
f | 40A three phase socket outlet as MK or approved equivalent | 1 | No. | 1500 | 1500
0
| FIRE ALARM |  |  |  | 0
g | Addressable smoke/heat detectors as Menvier code MAOH850 plus addressable base with code MAB800 or approved equivalent | 24 | No. | 7000 | 168000
| OTHER POINTS |  |  |  | 0
h | CCTV, Telephone,data & TV points in 20mm diameter Conduits | 5 | No. | 1100 | 5500
| Total carried forward to summary page ………. |  |  |  | 768700
ELECTRICAL INSTALLATION MAIN LV BOARD
Page BQ12
ALL RATES TO INCLUDE 16% VAT
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
SUB-MAINS POWER SUPPLY& DISTRIBUTION
| 600/1000 volt grade multi core PVC insulated copper armoured cable to BS 6346, including concealed heavy gauge PVC conduit, accessories and fittings |  |  |  | 0
a | 3 phase, 415V, Low Voltage Sub-board wall mounted fully front access chamber, with all CTs, auxilliary circuit breakers, labels, small wiring, ammeter and voltmeter, Automatic changeover switch, relays, timers, MANUAL-OFF-AUTOMATIC switch, indicator lamps, 1No. changeover contactors, and interconnections for automatic/ manual operation of the switch board. chamber sealable fabricated from 16 SWG steel sheets and frames complete with the following: | 1 | Item | 700000 | 700000
| (a) 400A TPN copper busbar | 1 | Set | 16500 | 16500
| (b) 400A TP&N isolator. | 1 | No. | 17500 | 17500
| (c) 200A TP & N MCCBs as ABB outgoers. | 3 | No. | 17700 | 53100
| (d) 1No. 400A TP MCCBAdjustable main incomer | 2 | No. | 15700 | 31400
(e) 34No. 125A Cut-out Fuses
(f) 4No. 63A MCCB DP
(g) Sufficient space for KPLC cut-outs.
(h) Sufficient space for No. KPLC 3 phase meter
(i) 415V three phase surge diverter
(j) Sufficient spare capacity for future development
(k) Sealable studs for all cover plate screws and all necessary accessories.
(l) 6mm perspex viewing window for meters.
(m) Heavy duty rubber lining for all the perspex viewing windows.
| (n) 6” Viro padlock complete with 3 sets of keys. |  |  |  | 0
| (k)20 KVAr automatic p.f Correction capacitor bank, with 5.steps regulators, CTs and control cabling | 1 | Item | 15000 | 15000
b | Complete earthing to KPLC requirements comprising clamps and 20mm dia, 4ft long copper earth electrodes in concrete inspection pit with removable cover. | 1 | Item | 50000 | 50000
c | 12 ways Distribution board DB with 200A Integral Isolator as Merlin Gerin complete With the following (10A,20A SP MCBs and 20A, 30A TP MCBs):- | 3 | Item | 55000 | 165000
d | 4-Core 25mm2 PVC/SWA/PVC cable from Sub-Board DB A ,B & C | 140 | Lm | 2000 | 280000
e | 9 ways Consumer Unit with 100A Integral Isolator as Merlin Gerin complete With the following (10A,20A SP MCBs and 20A, 30A SP MCBs):- | 6 | Item | 35000 | 210000
f | 2 x 16mm2+ 1x10mm2 cables from DB to the Consumer Units | 200 | Lm | 2000 | 400000
g | Wall mounted purpose made common KP&LC meter board manufactured in 14 SWG galvanized mild steel sheet and spray painted to approval, as shown on the schematic drawings, complete with the following:- | 1 | No. | 25000 | 25000
| (a) 1No. 200A TP MCCBAdjustable main incomer |  |  |  | 0
0
| (b) Totally enclosed Busbar chamber |  |  |  | 0
0
| (g) Sufficient space for KP&LC cut-outs |  |  |  | 0
| Total carried forward to price summary page ………. |  |  |  | 700000
SMATV INSTALLATION
Page 15
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
SMATV TRANSMISSION SYSTEM
a | 0.6 – 3.0 m solid aluminium dish antenna, C/Ku-band LNB with 8-way LNB (for Eutelsat, Intelsat, Atlantic Bird, HotBird) as per the technical specifications | 1 | No. | 16000 | 16000
b | Digital Channel processing modules as DSTV to process 50 No. digital programs from satellite dish or equal and approved equivalent as per the technical specifications | 1 | No. | 15000 | 15000
c | Signal Amplifiers (Boosters) and Filters | 2 | No. | 7500 | 15000
d | Floor Edge Modulation modules for converting the AV output of the above Satellite and Digital boxes to standard TV channels in PAL | 1 | No. | 5000 | 5000
e | TV/FM outlet socket with silver lining cover plate. | 19 | No. | 1000 | 19000
f | RG6 RF Coaxial Cables for signal distribution (305m per roll) | 2 | Rolls | 28000 | 56000
g | 22U Equipment rack Cabinet with shelves, casings, and mountings for SMATV System | 1 | No. | 40000 | 40000
h | 18 way RF Signal Splitters as per the technical specifications | 1 | No. | 5000 | 5000
i | Connectors, Mountings, and terminals | 1 | Lot | 100000 | 100000
j | Any other items necessary to complete the system installation satisfactorily. (List, give quantities and price of the items)
i)……………………………………………….
ii)………………………………………………
ii)…………………………………………..….
iv)……………………………..………………
TOTAL COST CARRIED FORWARD TO SUMMARY PAGE |  |  |  |  | 271000
ELECTRICAL INSTALLATION LIGHTNING PROTECTION
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ14
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
LIGHTNING PROTECTION
Supply, install, test and commission:
a | Air termination Type Furse RA225+RA600 fixed to ridge saddle Furse SD155 bolted to roof with water tight washers | 4 | No. | 8500 | 34000
0
0
b | 25x3mm copper tape TC030 on tape clip Furse CP210 fixed at 750mm intervals to approved detail | 100 | Lm | 1800 | 180000
0
0
c | Lugs including fixing bolts for roof conductors | 1 | Lot | 30000 | 30000
0
0
d | Test clamps Furse CN305 | 1 | Lot | 30000 | 30000
0
0
e | Earth rods Furse RC105 with driving sud, Furse ST015 and spike Furse SP015 driven in ground | 4 | No. | 5000 | 20000
0
f | 125x100x50mm deep boxes with cover and marked 'Safety Earth' installed in RC columns to approved details | 4 | No. | 5000 | 20000
0
0
g | Test and report complete installation for the compliance with KS04503 and BS code of practice BS6651 | 1 | Lot | 10000 | 10000
| Total carried forward to summary page... |  |  |  | 324000
ELECTRICAL INSTALLATION CLEAN POWER
| ALL RATES TO INCLUDE 16% VAT |  |  |  | Page BQ15
ITEM NO. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
KSHS
CLEAN POWER
Supply, install, test and commission:
a | 10KVA Freestanding Double-conversion (on-line) Uninteruptible Power Supply Unit, UPS as APC MGE Galaxy 300 or equal and approved equivalent, equiped with static and manual bypasses and having the following characteristics:- Redudancy: 10KVA Modules, Power Supply: 3-phase input 415V, Output Voltage: 1-phase output 240 V +/- 1%, Output Frequency: 50 Hz +/- 0.5 Hz, Overload Capacity: 125% for 1 minute, Overload Capacity: 125% for 1 minute, Input Power Factor: 1, V, Service life: Minimum 10 years, Backup time: Minimum 20 minutes, THD : < 2% linear Load, LOAD CF (max): 6:1, DC/AC Efficiency (nominal) :98%, AC/AC Efficiency (nominal) :96% | 1 | No. | 550000 | 550000
b | 12 Way CU with 100A isolator with 8No. 32A SP MCBs | 1 | No. | 35000 | 35000
0
0
0
0
0
0
0
| Total carried forward to summary page... |  |  |  | 585000
Page BQ16
SUMMARY OF TENDER PAGE
KAREN SDA Church
ELECTRICAL INSTALLATIONS
| Preliminaries: (Page 1)..…….……….………………...… |  | Kshs…...……….…………………… |  | 2258000
| Complying with specifications:.......………………...… |  | Kshs…...………………….………… |  | 40000
Total Brought Forward from :
| : Page 3 (Basement).…..……..………………….…. |  | KShs…..……..…………….………… |  | 722400
| : Page 5(Lower Ground).…..……..………………….…. |  | KShs…..……..…………….………… |  | 1915400
| : Page 7 (Ground Floor).…..……..………………….…. |  | KShs…..……..…………….………… |  | 1658800
| : Page 9 (First Floor)..…..……..………………….…. |  | KShs…..……..…………….………… |  | 1317000
| : Page 11 (Roof Plan)……..…..……..………………….…. |  | KShs…..……..…………….………… |  | 768700
| : Page 13(MAIN LV BOARD).…..……..………………….…. |  | KShs…..……..…………….………… |  | 700000
| : Page 14 (SMATV)..…………..…………….……………… |  | KShs…..……..…………….………… |  | 271000
| : Page 15 (LIGHTNING PROTECTION)..………………….…. |  | KShs…..……..…………….………… |  | 324000
| : Page 16 (CLEAN POWER)..………………….…. |  | KShs…..……..…………….………… |  | 585000
| Sub TotaI inclusive of VAT……………………………………… |  | Kshs………………………………….. |  | 10560300
| TOTAL CARRIED TO FORM OF TENDER………………….... |  | KShs…………………...………….. |  | 10560300
NB: Drawings are part of tender documents.Rates to include VAT and other relevant taxes
Name of Tenderer:............................................................................................
Address of Tenderer:.........................................................................................
| Signature and Stamp of Tenderer:.......................................... | Date: | …............................